## Worksheet
Label | Tendertext1
01APS-101 | Differential pressure switch Measuring range 200...1000 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Manufacturer Belimo Type 01APS-101
01APS-101.1 | Differential pressure switch Measuring range 200...1000 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² without tube and connection elements Multipack 45 pcs. Manufacturer Belimo Type 01APS-101.1
01APS-104 | Differential pressure switch Measuring range 500...2500 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Manufacturer Belimo Type 01APS-104
01APS-104.1 | Differential pressure switch Measuring range 500...2500 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² without tube and connection elements Multipack 45 pcs. Manufacturer Belimo Type 01APS-104.1
01APS-105 | Differential pressure switch Measuring range 1000...5000 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Manufacturer Belimo Type 01APS-105
01APS-10R | Differential pressure switch Measuring range 20...300 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Manufacturer Belimo Type 01APS-10R
01APS-10R.1 | Differential pressure switch Measuring range 20...300 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² without tube and connection elements Multipack 45 pcs. Manufacturer Belimo Type 01APS-10R.1
01APS-10U | Differential pressure switch Measuring range 50...500 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Manufacturer Belimo Type 01APS-10U
01APS-10U.1 | Differential pressure switch Measuring range 50...500 Pa NEMA 13 / IP54 Electrical connection Terminals for wire 0.5...1.5 mm² without tube and connection elements Multipack 45 pcs. Manufacturer Belimo Type 01APS-10U.1
01ATS-1040B | Frost monitor switch Auto reset Output signal Switch Capillary 3 m Degree of protection IEC/EN IP65 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 01ATS-1040B
01ATS-104XC | Frost monitor switch Manual reset Output signal Switch Capillary 3 m Degree of protection IEC/EN IP65 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 01ATS-104XC
01ATS-1050B | Frost monitor switch Auto reset Output signal Switch Capillary 6 m Degree of protection IEC/EN IP65 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 01ATS-1050B
01ATS-105XC | Frost monitor switch Manual reset Output signal Switch Capillary 6 m Degree of protection IEC/EN IP65 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 01ATS-105XC
01CT-1AH | Cable temperature sensor passive Output signal Pt100 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1AH
01CT-1ALF | Cable temperature sensor with mounting flange passive Output signal Pt100 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1ALF
01CT-1APF | Cable temperature sensor with mounting flange passive Output signal Pt100 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1APF
01CT-1BH | Cable temperature sensor passive Output signal Pt1000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1BH
01CT-1BLF | Cable temperature sensor with mounting flange passive Output signal Pt1000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1BLF
01CT-1BPF | Cable temperature sensor with mounting flange passive Output signal Pt1000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1BPF
01CT-1CH | Cable temperature sensor passive Output signal Ni1000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1CH
01CT-1CLF | Cable temperature sensor with mounting flange passive Output signal Ni1000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1CLF
01CT-1CPF | Cable temperature sensor with mounting flange passive Output signal Ni1000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1CPF
01CT-1DH | Cable temperature sensor passive Output signal Ni1000TK5000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1DH
01CT-1DLF | Cable temperature sensor with mounting flange passive Output signal Ni1000TK5000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1DLF
01CT-1DPF | Cable temperature sensor with mounting flange passive Output signal Ni1000TK5000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1DPF
01CT-1FH | Cable temperature sensor passive Output signal NTC1k8 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1FH
01CT-1LH | Cable temperature sensor passive Output signal NTC10k (10k2) Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1LH
01CT-1LLF | Cable temperature sensor with mounting flange passive Output signal NTC10k (10k2) Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1LLF
01CT-1LPF | Cable temperature sensor with mounting flange passive Output signal NTC10k (10k2) Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1LPF
01CT-1NH5 | Cable temperature sensor passive Output signal NTC10k Carel Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 6 m, 2-wire Manufacturer Belimo Type 01CT-1NH5
01CT-1QH | Cable temperature sensor passive Output signal NTC20k Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1QH
01CT-1QLF | Cable temperature sensor with mounting flange passive Output signal NTC20k Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1QLF
01CT-1QPF | Cable temperature sensor with mounting flange passive Output signal NTC20k Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP67 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01CT-1QPF
01DH-10N | Humidistat switch Auto reset Output signal Switch Probe length 156 mm Probe diameter 30 mm NEMA 13 / IP55 Electrical connection Screw terminal 1.5 mm² Manufacturer Belimo Type 01DH-10N
01DT-1AH | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AH
01DT-1AL | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AL
01DT-1AN | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AN
01DT-1AP | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AP
01DT-1AR | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AR
01DT-1AT | Duct/Immersion sensor Temperature passive Output signal Pt100 Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1AT
01DT-1BH | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BH
01DT-1BL | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BL
01DT-1BN | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BN
01DT-1BP | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BP
01DT-1BR | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BR
01DT-1BT | Duct/Immersion sensor Temperature passive Output signal Pt1000 Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1BT
01DT-1CH | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CH
01DT-1CL | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CL
01DT-1CN | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CN
01DT-1CP | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CP
01DT-1CR | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CR
01DT-1CT | Duct/Immersion sensor Temperature passive Output signal Ni1000 Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1CT
01DT-1DH | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DH
01DT-1DL | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DL
01DT-1DN | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DN
01DT-1DP | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DP
01DT-1DR | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DR
01DT-1DT | Duct/Immersion sensor Temperature passive Output signal Ni1000TK5000 Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1DT
01DT-1FL | Duct/Immersion sensor Temperature passive Output signal NTC1k8 Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1FL
01DT-1FN | Duct/Immersion sensor Temperature passive Output signal NTC1k8 Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1FN
01DT-1FP | Duct/Immersion sensor Temperature passive Output signal NTC1k8 Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1FP
01DT-1FR | Duct/Immersion sensor Temperature passive Output signal NTC1k8 Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1FR
01DT-1FT | Duct/Immersion sensor Temperature passive Output signal NTC1k8 Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1FT
01DT-1HP | Duct/Immersion sensor Temperature passive Output signal NTC5k Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1HP
01DT-1LH | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LH
01DT-1LL | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LL
01DT-1LN | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LN
01DT-1LP | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LP
01DT-1LR | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LR
01DT-1LT | Duct/Immersion sensor Temperature passive Output signal NTC10k (10k2) Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1LT
01DT-1MN | Duct/Immersion sensor Temperature passive Output signal NTC10k Pre (10k3) Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1MN
01DT-1MP | Duct/Immersion sensor Temperature passive Output signal NTC10k Pre (10k3) Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1MP
01DT-1NN | Duct/Immersion sensor Temperature passive Output signal NTC10k Carel Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1NN
01DT-1QH | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QH
01DT-1QL | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QL
01DT-1QN | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QN
01DT-1QP | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QP
01DT-1QR | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QR
01DT-1QT | Duct/Immersion sensor Temperature passive Output signal NTC20k Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01DT-1QT
01HT-101CA | Temperature monitor TW passive Auto reset Output signal Switch Capillary 1 m Degree of protection IEC/EN IP54 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 01HT-101CA
01HT-1A | Contact temperature sensor passive Output signal Pt100 NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1A
01HT-1B | Contact temperature sensor passive Output signal Pt1000 NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1B
01HT-1C | Contact temperature sensor passive Output signal Ni1000 NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1C
01HT-1D | Contact temperature sensor passive Output signal Ni1000TK5000 NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1D
01HT-1F | Contact temperature sensor passive Output signal NTC1k8 NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1F
01HT-1L | Contact temperature sensor passive Output signal NTC10k (10k2) NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1L
01HT-1Q | Contact temperature sensor passive Output signal NTC20k NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01HT-1Q
01MT-1B4 | Average temperature sensor passive Output signal Pt1000 Probe length 3 m NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01MT-1B4
01MT-1B5 | Average temperature sensor passive Output signal Pt1000 Probe length 6 m NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01MT-1B5
01PT-1BH | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Pt1000 Probe length 50 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1BH
01PT-1BL | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Pt1000 Probe length 100 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1BL
01PT-1BP | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Pt1000 Probe length 200 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1BP
01PT-1DH | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Ni1000TK5000 Probe length 50 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1DH
01PT-1DL | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Ni1000TK5000 Probe length 100 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1DL
01PT-1DP | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal Ni1000TK5000 Probe length 200 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1DP
01PT-1LH | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal NTC10k (10k2) Probe length 50 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1LH
01PT-1LL | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal NTC10k (10k2) Probe length 100 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1LL
01PT-1LP | Immersion temperature sensor with fast response characteristics passive Direct immersion with stainless steel probe and R 1/2” connection Output signal NTC10k (10k2) Probe length 200 mm Probe diameter 6/4 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01PT-1LP
01RT-1B-0 | Room sensor Temperature passive Output signal Pt1000 Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1B-0
01RT-1C-0 | Room sensor Temperature passive Output signal Ni1000 Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1C-0
01RT-1D-0 | Room sensor Temperature passive Output signal Ni1000TK5000 Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1D-0
01RT-1F-0 | Room sensor Temperature passive Output signal NTC1k8 Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1F-0
01RT-1L-0 | Room sensor Temperature passive Output signal NTC10k (10k2) Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1L-0
01RT-1M-0 | Room sensor Temperature passive Output signal NTC10k Pre (10k3) Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1M-0
01RT-1Q-0 | Room sensor Temperature passive Output signal NTC20k Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type 01RT-1Q-0
01ST-1A3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal Pt100 Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1A3
01ST-1B3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal Pt1000 Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1B3
01ST-1C3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal Ni1000 Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1C3
01ST-1D3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal Ni1000TK5000 Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1D3
01ST-1F3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal NTC1k8 Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1F3
01ST-1L3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal NTC10k (10k2) Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1L3
01ST-1Q3 | Contact temperature sensor passive With fixing strap for pipes up to ø110 mm Output signal NTC20k Probe diameter 6 mm Degree of protection IEC/EN IP65 Electrical connection Cable 2 m, 2-wire Manufacturer Belimo Type 01ST-1Q3
01UT-1A | Outdoor sensor Temperature passive Internal sensor Output signal Pt100 NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1A
01UT-1A0X | Outdoor sensor Temperature passive External sensor Output signal Pt100 Probe length 25 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1A0X
01UT-1B | Outdoor sensor Temperature passive Internal sensor Output signal Pt1000 NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1B
01UT-1B0X | Outdoor sensor Temperature passive External sensor Output signal Pt1000 Probe length 25 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1B0X
01UT-1C | Outdoor sensor Temperature passive Internal sensor Output signal Ni1000 NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1C
01UT-1D | Outdoor sensor Temperature passive Internal sensor Output signal Ni1000TK5000 NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1D
01UT-1F | Outdoor sensor Temperature passive Internal sensor Output signal NTC1k8 NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1F
01UT-1L | Outdoor sensor Temperature passive Internal sensor Output signal NTC10k (10k2) NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1L
01UT-1N | Outdoor sensor Temperature passive Internal sensor Output signal NTC10k Carel NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1N
01UT-1Q | Outdoor sensor Temperature passive Internal sensor Output signal NTC20k NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 01UT-1Q
20DTS-1P3 | Frost monitor active Auto or manual reset Display type LED Nominal voltage AC 24 V Output signal Switch, 0...10 V Measured values Temperature, Frost Adjustment range 1...10°C Capillary 2 m Degree of protection IEC/EN IP42 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 20DTS-1P3
20DTS-1P5 | Frost monitor active Auto or manual reset Display type LED Nominal voltage AC 24 V Output signal Switch, 0...10 V Measured values Temperature, Frost Adjustment range 1...10°C Capillary 6 m Degree of protection IEC/EN IP42 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type 20DTS-1P5
22ADP-124D | Differential pressure sensor Air dual 2 measuring systems Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-124D
22ADP-124F | Differential pressure sensor Air dual 2 measuring systems Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-124F
22ADP-154 | Differential pressure sensor Air Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154
22ADP-154D | Differential pressure sensor Air dual 2 measuring systems Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154D
22ADP-154F | Differential pressure sensor Air dual 2 measuring systems Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154F
22ADP-154H | Differential pressure sensor Air dual with two additional inputs 2 measuring systems Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154H
22ADP-154K | Differential pressure sensor Air dual with two additional inputs 2 measuring systems Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 4 duct connectors (plastic), incl. 2x 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154K
22ADP-154L | Differential pressure sensor Air Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Display type LCD Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-154L
22ADP-156 | Differential pressure sensor Air Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-156
22ADP-156L | Differential pressure sensor Air Display type LCD Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Display type LCD Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-156L
22ADP-15Q | Differential pressure sensor Air Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-15Q
22ADP-15QA | Differential pressure sensor Air Auto-Zero Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-15QA
22ADP-15QB | Differential pressure sensor Air Auto-Zero Display type LCD Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Display type LCD Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-15QB
22ADP-15QL | Differential pressure sensor Air Display type LCD Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Display type LCD Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-15QL
22ADP-164 | Differential pressure sensor Air Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal BACnet, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-164
22ADP-164L | Differential pressure sensor Air Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal BACnet, 0...5 V, 0...10 V Measured values Differential pressure, Volumetric flow Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-164L
22ADP-184 | Differential pressure sensor Air Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-184
22ADP-184A | Differential pressure sensor Air Auto-Zero Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-184A
22ADP-184B | Differential pressure sensor Air Auto-Zero Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-184B
22ADP-184L | Differential pressure sensor Air Display type LCD Measuring range -100...2500 Pa Measuring range -0.4...10 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-184L
22ADP-186 | Differential pressure sensor Air Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-186
22ADP-186A | Differential pressure sensor Air Auto-Zero Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-186A
22ADP-186B | Differential pressure sensor Air Auto-Zero Display type LCD Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-186B
22ADP-186L | Differential pressure sensor Air Display type LCD Measuring range 0...7000 Pa Measuring range 0...28 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-186L
22ADP-18Q | Differential pressure sensor Air Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-18Q
22ADP-18QA | Differential pressure sensor Air Auto-Zero Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-18QA
22ADP-18QB | Differential pressure sensor Air Auto-Zero Display type LCD Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-18QB
22ADP-18QL | Differential pressure sensor Air Display type LCD Measuring range -150...250 Pa Measuring range -0.6...1 inch WC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 4...20 mA Display type LCD Measured values Differential pressure Multirange 8 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Incl. 2 duct connectors (plastic), incl. 2 m tube (PVC) Incl. mounting plate, incl. mounting kit Manufacturer Belimo Type 22ADP-18QL
22CT-12H | Cable temperature sensor Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22CT-12H
22CT-14H | Cable temperature sensor Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22CT-14H
22DC-11 | Duct sensor CO₂ Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂ Probe length 150 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DC-11
22DC-110L | Duct sensor CO₂ / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, NTC10k (10k2) Output signal passive temperature NTC10k (10k2) Measured values CO₂, Temperature Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DC-110L
22DC-13 | Duct sensor CO₂ Nominal voltage AC/DC 24 V Output signal 4...20 mA, 0...5 V, 0...10 V Measured values CO₂ Probe length 150 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DC-13
22DCK-11 | Duct sensor CO₂ / VOC / CO₂+VOC mix / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂, VOC, Temperature Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DCK-11
22DCM-11 | Duct sensor CO₂ / VOC / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂, VOC, Temperature Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DCM-11
22DCV-11 | Duct sensor CO₂ / VOC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂, VOC Probe length 150 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DCV-11
22DT-12H | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12H
22DT-12L | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12L
22DT-12N | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12N
22DT-12P | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12P
22DT-12R | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12R
22DT-12T | Duct/Immersion sensor Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-12T
22DT-14H | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 50 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14H
22DT-14L | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 100 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14L
22DT-14N | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 150 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14N
22DT-14P | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 200 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14P
22DT-14R | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 300 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14R
22DT-14T | Duct/Immersion sensor Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 450 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DT-14T
22DTC-11 | Duct sensor CO₂ / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂, Temperature Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTC-11
22DTC-13 | Duct sensor CO₂ / Temperature Nominal voltage AC/DC 24 V Output signal 4...20 mA, 0...5 V, 0...10 V Measured values CO₂, Temperature Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTC-13
22DTH-11M | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature, Humidity Multirange 4 measuring ranges selectable Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-11M
22DTH-11MM | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, NTC10k Pre (10k3) Output signal passive temperature NTC10k Pre (10k3) Measured values Temperature, Humidity Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-11MM
22DTH-11MN | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, NTC10k Carel Output signal passive temperature NTC10k Carel Measured values Temperature, Humidity Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-11MN
22DTH-11Q | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature, Humidity Multirange 4 measuring ranges selectable Probe length 270 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-11Q
22DTH-13M | Duct sensor Humidity / Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature, Humidity Multirange 4 measuring ranges selectable Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-13M
22DTH-13Q | Duct sensor Humidity / Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature, Humidity Multirange 4 measuring ranges selectable Probe length 270 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-13Q
22DTH-15M | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Temperature, Humidity Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-15M
22DTH-15Q | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Temperature, Humidity Probe length 270 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-15Q
22DTH-16M | Duct sensor Humidity / Temperature Nominal voltage AC/DC 24 V Output signal BACnet, 0...5 V, 0...10 V Measured values Temperature, Humidity Probe length 140 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTH-16M
22DTM-11 | Duct sensor CO₂ / Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values CO₂, Temperature, Humidity Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTM-11
22DTM-1106 | Duct sensor CO₂ / Humidity / Temperature Display type LCD Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Display type LCD Measured values CO₂, Temperature, Humidity Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTM-1106
22DTM-15 | Duct sensor CO₂ / Humidity / Temperature Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values CO₂, Temperature, Humidity Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTM-15
22DTM-16 | Duct sensor CO₂ / Humidity / Temperature Nominal voltage AC/DC 24 V Output signal BACnet, 0...5 V, 0...10 V Measured values CO₂, Temperature, Humidity Probe length 180 mm Probe diameter 19.5 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22DTM-16
22HH-10 | Condensation Switch Internal sensor Display type LED Nominal voltage AC/DC 24 V Output signal Switch Measured values Condensation NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HH-10
22HH-100S-6 | Condensation Switch External sensor Cable length 7 m Display type LED Nominal voltage AC/DC 24 V Output signal Switch Measured values Condensation NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HH-100S-6
22HH-100S-7 | Condensation Switch External sensor Cable length 12 m Display type LED Nominal voltage AC/DC 24 V Output signal Switch Measured values Condensation NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HH-100S-7
22HH-100X | Condensation Switch External sensor Cable length 2 m Display type LED Nominal voltage AC/DC 24 V Output signal Switch Measured values Condensation NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HH-100X
22HL-10 | Leakage switch Auto reset Nominal voltage AC/DC 24 V Output signal Switch Measured values Leakage detection NEMA 4 / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HL-10
22HT-12 | Contact temperature sensor Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HT-12
22HT-14 | Contact temperature sensor Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable NEMA 1 / IP54 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HT-14
22HTH-110X | Contact sensor Humidity / Temperature Cable length 2 m Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature, Humidity NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22HTH-110X
22MT-125 | Average temperature sensor Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 6 m NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22MT-125
22MT-144 | Average temperature sensor Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 3 m NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22MT-144
22MT-145 | Average temperature sensor Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 6 m NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22MT-145
22PDP-185 | Differential pressure sensor Water Display type LCD Measuring range 0...5 bar Nominal voltage AC/DC 24 V Output signal 4...20 mA, 0...5 V, 0...10 V Measured values Differential pressure Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22PDP-185
22PDP-186 | Differential pressure sensor Water Display type LCD Measuring range 0...10 bar Nominal voltage AC/DC 24 V Output signal 4...20 mA, 0...5 V, 0...10 V Measured values Differential pressure Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22PDP-186
22PDP-189 | Differential pressure sensor Water Display type LCD Measuring range 0...35 bar Nominal voltage AC/DC 24 V Output signal 4...20 mA, 0...5 V, 0...10 V Measured values Differential pressure Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22PDP-189
22PE-1UC | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 15, PN 25 Nominal voltage AC/DC 24 V External thread, G 3/4" qp 1.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UC
22PE-1UD | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 20, PN 25 Nominal voltage AC/DC 24 V External thread, G 1" qp 2.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UD
22PE-1UE | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 25, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/4" qp 3.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UE
22PE-1UF | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 32, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/2" qp 6 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UF
22PE-1UG | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 40, PN 25 Nominal voltage AC/DC 24 V External thread, G 2" qp 10 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UG
22PE-1UH | Thermal energy meter Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 50, PN 25 Nominal voltage AC/DC 24 V External thread, G 2 1/2" qp 15 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Manufacturer Belimo Type 22PE-1UH
22PEM-1UC | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 15, PN 25 Nominal voltage AC/DC 24 V External thread, G 3/4" qp 1.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UC
22PEM-1UD | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 20, PN 25 Nominal voltage AC/DC 24 V External thread, G 1" qp 2.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UD
22PEM-1UE | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 25, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/4" qp 3.5 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UE
22PEM-1UF | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 32, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/2" qp 6 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UF
22PEM-1UG | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 40, PN 25 Nominal voltage AC/DC 24 V External thread, G 2" qp 10 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UG
22PEM-1UH | Thermal energy meter MID / EN 1434 Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 50, PN 25 Nominal voltage AC/DC 24 V External thread, G 2 1/2" qp 15 m³/h BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PEM-1UH
22PF-1UC | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 15, PN 25 Nominal voltage AC/DC 24 V External thread, G 3/4" FS 0.5 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UC
22PF-1UD | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 20, PN 25 Nominal voltage AC/DC 24 V External thread, G 1" FS 0.83 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UD
22PF-1UE | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 25, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/4" FS 1.17 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UE
22PF-1UF | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 32, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/2" FS 2.0 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UF
22PF-1UG | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 40, PN 25 Nominal voltage AC/DC 24 V External thread, G 2" FS 3.33 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UG
22PF-1UH | Flow sensor Ultrasonic volumetric flow measurement NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 50, PN 25 Nominal voltage AC/DC 24 V External thread, G 2 1/2" FS 5.0 l/s BACnet MS/TP, Modbus RTU, MP-Bus Manufacturer Belimo Type 22PF-1UH
22RT-18-1 | Room sensor Temperature active NFC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RT-18-1
22RT-19-1 | Room sensor Temperature active NFC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RT-19-1
22RTH-18-1 | Room sensor Humidity / Temperature NFC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RTH-18-1
22RTH-19-1 | Room sensor Humidity / Temperature NFC Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RTH-19-1
22RTM-18-1 | Room sensor CO₂ / Humidity / Temperature NFC Display type LED Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RTM-18-1
22RTM-19-1 | Room sensor CO₂ / Humidity / Temperature NFC Display type LED Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type 22RTM-19-1
22UT-12 | Outdoor sensor Temperature External sensor Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature Multirange 8 measuring ranges selectable Probe length 25 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UT-12
22UT-14 | Outdoor sensor Temperature External sensor Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature Multirange 8 measuring ranges selectable Probe length 25 mm Probe diameter 6 mm NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UT-14
22UTH-11 | Outdoor sensor with weather shield Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature, Humidity Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-11
22UTH-110M | Outdoor sensor with weather shield Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, NTC10k Pre (10k3) Output signal passive temperature NTC10k Pre (10k3) Measured values Temperature, Humidity NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-110M
22UTH-110X | Outdoor sensor with weather and radiated heat shield Humidity / Temperature Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V Measured values Temperature, Humidity Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-110X
22UTH-13 | Outdoor sensor with weather shield Humidity / Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature, Humidity Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-13
22UTH-130X | Outdoor sensor with weather and radiated heat shield Humidity / Temperature Nominal voltage DC 24 V Output signal 4...20 mA Measured values Temperature, Humidity Multirange 4 measuring ranges selectable NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-130X
22UTH-150X | Outdoor sensor with weather and radiated heat shield Humidity / Temperature Nominal voltage AC/DC 24 V Output signal Modbus, 0...5 V, 0...10 V Measured values Temperature, Humidity NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-150X
22UTH-160X | Outdoor sensor with weather and radiated heat shield Humidity / Temperature Nominal voltage AC/DC 24 V Output signal BACnet, 0...5 V, 0...10 V Measured values Temperature, Humidity NEMA 4X / IP65 Electrical connection Pluggable spring loaded terminal block max. 2.5 mm² Manufacturer Belimo Type 22UTH-160X
22WDP-111 | Differential pressure sensor Water Measuring range 0...1 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-111
22WDP-112 | Differential pressure sensor Water Measuring range 0...2.5 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-112
22WDP-114 | Differential pressure sensor Water Measuring range 0...4 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-114
22WDP-115 | Differential pressure sensor Water Measuring range 0...6 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-115
22WDP-131 | Differential pressure sensor Water Measuring range 0...1 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-131
22WDP-132 | Differential pressure sensor Water Measuring range 0...2.5 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-132
22WDP-134 | Differential pressure sensor Water Measuring range 0...4 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-134
22WDP-135 | Differential pressure sensor Water Measuring range 0...6 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Differential pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WDP-135
22WP-114 | Pressure sensor liquids Measuring range 0...4 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-114
22WP-115 | Pressure sensor liquids Measuring range 0...6 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-115
22WP-116 | Pressure sensor liquids Measuring range 0...10 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-116
22WP-117 | Pressure sensor liquids Measuring range 0...16 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-117
22WP-119 | Pressure sensor liquids Measuring range 0...25 bar Nominal voltage AC/DC 24 V Output signal 0...10 V Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-119
22WP-134 | Pressure sensor liquids Measuring range 0...4 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-134
22WP-135 | Pressure sensor liquids Measuring range 0...6 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-135
22WP-136 | Pressure sensor liquids Measuring range 0...10 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-136
22WP-137 | Pressure sensor liquids Measuring range 0...16 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-137
22WP-139 | Pressure sensor liquids Measuring range 0...25 bar Nominal voltage DC 24 V Output signal 4...20 mA Measured values Relative pressure NEMA 4 / IP65 Electrical connection Connector plug for wire 0.5...1.5 mm² Manufacturer Belimo Type 22WP-139
A-22AP-A02 | Duct connector Metal L 40 mm Tube connection 5 mm
A-22AP-A04 | Duct connector Metal L 100 mm Tube connection 5 mm
A-22AP-A05.1 | Duct connector kit Tube: PVC transparent Duct connector: ABS grey Screws: galvanized steel for 01APS-.. PVC tube 2 m 2x duct connector (plastic) Multipack 50 pcs.
A-22AP-A06 | Mounting bracket Metal 18x60x55 mm (LxWxH) L form for 01APS-..
A-22AP-A07 | Mounting bracket Metal 10x60x70 mm (LxWxH) S form for 01APS-..
A-22AP-A08 | Duct connector kit for 22ADP-.. PVC tube 2 m 2x duct connector (plastic)
A-22AP-A09.1 | Duct connector Plastic L 80 mm for 01APS-.. Tube connection 6 mm Multipack 90 pcs.
A-22AP-A11.1 | Cable entry M20x1.5 for 01APS-.. Multipack 10 pcs.
A-22D-A03 | Mounting flange Plastic for sensor probe 6 mm up to max. 120°C [248°F]
A-22D-A05 | Mounting flange Brass for sensor probe 6 mm up to max. 260°C
A-22D-A06 | Replacement filter Stainless steel sensor probe tip wire mesh
A-22D-A08 | Mounting kit with 6 mounting brackets
A-22D-A09 | Mounting plate S housing
A-22D-A10 | Mounting plate L housing
A-22D-A11 | Mounting clip with screws and adhesive foil
A-22D-A12 | Mounting flange Plastic for frost guard 20DTS-..
A-22D-A35 | Mounting flange Plastic for duct sensor 19.5 mm up to max. 120°C [248°F]
A-22G-A01.1 | Connection adapter flex conduit M20x1.5 for cable gland 1x 6 mm Multipack 10 pcs.
A-22G-A02.1 | Connection adapter flex conduit M20 for cable gland 2x 6 mm Multipack 10 pcs.
A-22G-A05 | Bluetooth dongle for Belimo Duct Sensor Assistant App certified and available in North America, European Union, EFTA States and UK
A-22P-A06 | Thermowell Stainless steel 50 mm G 1/2", SW27
A-22P-A08 | Thermowell Stainless steel 100 mm G 1/2", SW27
A-22P-A10 | Thermowell Stainless steel 150 mm G 1/2", SW27
A-22P-A12 | Thermowell Stainless steel 200 mm G 1/2", SW27
A-22P-A14 | Thermowell Stainless steel 300 mm G 1/2", SW27
A-22P-A16 | Thermowell Stainless steel 450 mm G 1/2", SW27
A-22P-A18 | Thermowell Brass 50 mm R 1/2", SW22
A-22P-A20 | Thermowell Brass 100 mm R 1/2", SW22
A-22P-A22 | Thermowell Brass 150 mm R 1/2", SW22
A-22P-A24 | Thermowell Brass 200 mm R 1/2", SW22
A-22P-A26 | Thermowell Brass 300 mm R 1/2", SW22
A-22P-A28 | Thermowell Brass 450 mm R 1/2", SW22
A-22P-A29 | Thermowell Stainless steel 250 mm G 1/2", SW27
A-22P-A30 | Thermowell Brass 250 mm R 1/2", SW22
A-22P-A44 | Thermal contact fluid
A-22P-A45 | Compression fitting G 1/4" (external thread) for 6 mm with cutting ring Stainless steel
A-22P-A47 | Fixing strap for pipes ø20...110 mm [0.8...4.3"]
A-22P-A49 | Fixing strap for pipes ø20...250 mm [0.8...9.8"]
A-22P-A51 | Cold barrier Plastic L 50 mm for thermowell A-22P-A..
A-22P-A53 | Adapter for Siemens thermowell with thermal contact fluid
A-22P-A61 | Thermowell kit incl. probe fixing material Brass nickel-plated 100 mm G 1/2", SW22
A-22P-A62 | Thermowell kit incl. probe fixing material Brass nickel-plated 150 mm G 1/2", SW22
A-22P-A63 | Thermowell kit incl. probe fixing material Brass nickel-plated 200 mm G 1/2", SW22
A-22P-A64 | Thermowell kit incl. probe fixing material Stainless steel 100 mm G 1/2", SW22
A-22P-A65 | Thermowell kit incl. probe fixing material Stainless steel 150 mm G 1/2", SW22
A-22P-A66 | Thermowell kit incl. probe fixing material Stainless steel 200 mm G 1/2", SW22
A-22PE-A01 | T-piece DN 15 with thermowell
A-22PE-A02 | T-piece DN 20 with thermowell
A-22PE-A03 | T-piece DN 25 with thermowell
A-22PE-A04 | T-piece DN 32 with thermowell
A-22PE-A05 | T-piece DN 40 with thermowell
A-22PE-A06 | T-piece DN 50 with thermowell
A-22PE-A07 | Thermowell Stainless steel 50 mm G 1/4", SW17
A-22PE-A08 | Thermowell Stainless steel 80 mm G 1/2", SW27
A-22PEM-A01 | Insulation shell for thermal energy meter 2-way DN 15...25 only for non-condensing applications
A-22PEM-A02 | Insulation shell for thermal energy meter 2-way DN 32...50 only for non-condensing applications
A-22PEM-A03 | Security seal with wire Set of 2 pcs.
A-22PEM-A04 | Grommet for RJ connection module with clamp
A-22PEM-A06 | T-piece DN 15 M10x1 for external direct immersion temperature sensor T1
A-22PEM-A07 | T-piece DN 20 M10x1 for external direct immersion temperature sensor T1
A-22PEM-A08 | T-piece DN 25 M10x1 for external direct immersion temperature sensor T1
A-22PEM-A09 | T-piece DN 32 M10x1 for external direct immersion temperature sensor T1
A-22PEM-A10 | T-piece DN 40 M10x1 for external direct immersion temperature sensor T1
A-22PEM-A11 | T-piece DN 50 M10x1 for external direct immersion temperature sensor T1
A-22U-A01 | Rain cover for 22UTH-..
A-22WP-A02 | Reduction adapter G 1/4" (internal thread) to G 1/2" (external thread)
A-22WP-A04 | Pipe connector Brass Pipe 6 mm to G 1/4" (external thread) Set of 2 pcs.
A-22WP-A06 | Pipe connector Stainless steel Pipe 6 mm to G 1/4" (external thread) Set of 2 pcs.
A-22WP-A08 | Pipe connector Brass Pipe 8 mm to G 1/4" (external thread) Set of 2 pcs.
A-22WP-A10 | Pipe connector Stainless steel Pipe 8 mm to G 1/4" (external thread) Set of 2 pcs.
A-22WP-A11 | Mounting bracket Metal 40x60x40 mm (LxWxH) for 22WDP-..
AH-20 | Actuator arm Galvanised steel for standard shaft clamp (reversible) Slot width 8.2 mm
AH-25 | Actuator arm Galvanised steel for standard shaft clamp (one-sided) Slot width 8.2 mm
AH-GMA | Actuator arm Galvanised steel for standard shaft clamp clamping range ø12...26 mm Slot width 8.2 mm
AH-TF | Actuator arm Thermo-plastic material for TF.. Slot width 8.2 mm
AV12-25-I | Shaft extension 240 mm ø20 mm clamping range ø12...21 mm for CrNi shaft (INOX) Galvanised steel
AV6-20 | Shaft extension 170 mm ø10 mm clamping range ø6...16 mm Galvanised steel
AV8-25 | Shaft extension 240 mm ø20 mm clamping range ø8...22.7 mm Galvanised steel
AVK230A-3 | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6.5 VA Control 3-point Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type AVK230A-3
AVK230A-3-RE | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6.5 VA Control 3-point Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type AVK230A-3-RE
AVK24A-3-RE | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2000 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control 3-point Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Manual override with push-button Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-3-RE
AVK24A-3-TPC | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2000 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control 3-point Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-3-TPC
AVK24A-MOD | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-MOD
AVK24A-MP-RE | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-MP-RE
AVK24A-MP-TPC | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-MP-TPC
AVK24A-SR-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-SR-TPC
AVK24A-SZ-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating Running time motor 150 s / 32 mm Running time fail-safe 35 s / 32 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type AVK24A-SZ-TPC
BAT72 | Thermoelectric tripping device AC/DC 24 V, Cable 1 m Duct inside temperature 72°C (colour black) Duct outside temperature 72°C Probe length 65 mm with control key
BAT72-ST | Thermoelectric tripping device AC/DC 24 V, Cable with connector plug 1 m Duct inside temperature 72°C (colour black) Duct outside temperature 72°C Probe length 65 mm with control key, with plug
BAT72/9 | Thermoelectric tripping device AC/DC 24 V, Cable 1 m Duct inside temperature 72°C (colour black) Duct outside temperature 72°C Probe length 90 mm with control key
BE230 | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 0.5 W Power consumption for wire sizing 15 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable 1 m Form fit 14x14 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE230
BE230-12 | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 0.5 W Power consumption for wire sizing 15 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE230-12
BE24 | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 12 W Power consumption in rest position 0.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable 1 m Form fit 14x14 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE24
BE24-12 | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 12 W Power consumption in rest position 0.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE24-12
BE24-12-ST | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 12 W Power consumption in rest position 0.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE24-12-ST
BE24-ST | Smoke control damper actuator Current reduction in rest position Constant, load-independent running time Torque motor 40 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 12 W Power consumption in rest position 0.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT (3° / 87°) Cable with connector plug 1 m Form fit 14x14 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BE24-ST
BEE230 | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 25 Nm Running time motor 60 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEE230
BEE24 | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 25 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.1 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEE24
BEE24-SR | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 25 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 5.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEE24-SR
BEE24-ST | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 25 Nm Running time motor 60 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.1 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEE24-ST
Belimo Assistant 2 | Belimo Assistant 2 Platform-independent for Android, iOS and Windows
Belimo Assistant App | Belimo Assistant App Smartphone app for easy commissioning, configuration and maintenance (Android smartphones only)
Belimo Display App | Belimo Display App Innovative end-user app for displaying current room values and adjusting setpoints. For NFC-capable Android and iOS smartphones. Compatible devices: 22RT.. and P-22RT...
Belimo Duct Sensor Assistant App | Belimo Duct Sensor Assistant App Smartphone app for easy commissioning, configuration and maintenance (Android smartphones only) only works with Bluetooth dongle A-22G-A05 available in North America, European Union, EFTA States and UK
BEN230 | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 15 Nm Running time motor 30 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 0.4 W Power consumption for wire sizing 7 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEN230
BEN24 | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 15 Nm Running time motor 30 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.1 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEN24
BEN24-SR | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 15 Nm Running time motor 30 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 6.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEN24-SR
BEN24-ST | Smoke control damper actuator Mechanical safety lock Current reduction in rest position Constant, load-independent running time Torque motor 15 Nm Running time motor 30 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.1 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with hand crank Direction of motion selectable by mounting Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BEN24-ST
BF120-2 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 120 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF120-2
BF230 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230
BF230-2 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF230-2
BF230-2/500 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF230-2/500
BF230-C134 | Fire damper actuator Current reduction in rest position Torque motor 20 Nm Running time motor 60 s Torque fail-safe 20 Nm Running time fail-safe <30 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-C134
BF230-C232 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 20 Nm Running time motor 60 s Torque fail-safe 20 Nm Running time fail-safe <30 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-C232
BF230-C93 | Fire damper actuator Current reduction in rest position Special version Silicone cable Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-C93
BF230-RE | Fire damper actuator Current reduction in rest position Torque motor 15 Nm Running time motor 75 s Torque fail-safe 15 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3.5 W Power consumption for wire sizing 12 VA Control Open/close Auxiliary switch 2x SPDT (<10° (fix) / >30°...90° (adjustable)) Cable 1 m Universal shaft clamp 3/4" Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Anti-rotation bracket Manufacturer Belimo Type BF230-RE
BF230-TN | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-TN
BF230-TN-2 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF230-TN-2
BF230-TN-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-TN-ST
BF230-TN/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-TN/300
BF230-TN/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230-TN/500
BF230/300 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230/300
BF230/500 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF230/500
BF24 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24
BF24-2 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF24-2
BF24-2-ST | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF24-2-ST
BF24-C134 | Fire damper actuator Current reduction in rest position Torque motor 20 Nm Running time motor 60 s Torque fail-safe 20 Nm Running time fail-safe <30 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 10 W Power consumption in rest position 2 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-C134
BF24-C232 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 20 Nm Running time motor 60 s Torque fail-safe 20 Nm Running time fail-safe <30 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 10 W Power consumption in rest position 2 W Power consumption for wire sizing 12.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-C232
BF24-RE | Fire damper actuator Current reduction in rest position Torque motor 15 Nm Running time motor 75 s Torque fail-safe 15 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (<10° (fix) / >30°...90° (adjustable)) Cable 1 m Universal shaft clamp 3/4" Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Anti-rotation bracket Manufacturer Belimo Type BF24-RE
BF24-SR | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-SR
BF24-SR-TN | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 9.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-SR-TN
BF24-ST | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-ST
BF24-ST-RE | Fire damper actuator Current reduction in rest position Torque motor 15 Nm Running time motor 75 s Torque fail-safe 15 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Auxiliary switch 2x SPDT (<10° (fix) / >30°...90° (adjustable)) Cable with connector plug 1 m Universal shaft clamp 3/4" Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Anti-rotation bracket Manufacturer Belimo Type BF24-ST-RE
BF24-TN | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-TN
BF24-TN-2 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF24-TN-2
BF24-TN-2-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BF24-TN-2-ST
BF24-TN-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-TN-ST
BF24-TN-ST/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 3 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-TN-ST/300
BF24-TN/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24-TN/500
BF24/500 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 2 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24/500
BF24TL-TN-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control Open/close, communicative Electrical connection Cable with connector plug 1 m, with plug Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24TL-TN-ST
BF24TL-TN-ST-2 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control Open/close, communicative Electrical connection Cable with connector plug 1 m, with plug Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF24TL-TN-ST-2
BF48-5 | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 48 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3.5 W Power consumption for wire sizing 16 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF48-5
BF48-5-ST | Fire damper actuator Current reduction in rest position Torque motor 18 Nm Running time motor 120 s Torque fail-safe 12 Nm Running time fail-safe 16 s Nominal voltage AC/DC 48 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3.5 W Power consumption for wire sizing 16 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, non-continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BF48-5-ST
BFL230 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.9 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230
BFL230-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.1 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230-T
BFL230-T-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.1 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230-T-ST
BFL230-T/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.1 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230-T/300
BFL230-T/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.1 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230-T/500
BFL230/300 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.9 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL230/300
BFL24 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.7 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24
BFL24-SR | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-SR
BFL24-SR-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-SR-T
BFL24-ST | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.7 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-ST
BFL24-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T
BFL24-T-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T-ST
BFL24-T-ST/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T-ST/300
BFL24-T-ST/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T-ST/500
BFL24-T/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T/300
BFL24-T/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T/500
BFL24-T95 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 4 Nm Running time motor 60 s Torque fail-safe 3 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.8 W Power consumption for wire sizing 4 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag, Form fit insert 12/10 mm Manufacturer Belimo Type BFL24-T95
BFN230 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230
BFN230-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.1 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230-T
BFN230-T-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.1 W Power consumption for wire sizing 10 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230-T-ST
BFN230-T/300 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230-T/300
BFN230-T/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230-T/500
BFN230/300 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230/300
BFN230/500 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN II, reinforced insulation Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN230/500
BFN24 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24
BFN24-SR | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-SR
BFN24-SR-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.7 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-SR-T
BFN24-SR/050 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT (5° / 80°) Cable 0.5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-SR/050
BFN24-ST | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-ST
BFN24-T | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T
BFN24-T-ST | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 1 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T-ST
BFN24-T-ST/300 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 3 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T-ST/300
BFN24-T-ST/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable with connector plug 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T-ST/500
BFN24-T/050 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 0.5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T/050
BFN24-T/500 | Fire damper actuator with thermoelectric tripping device BAT (72°C) Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24-T/500
BFN24/500 | Fire damper actuator Mechanical safety lock Current reduction in rest position Torque motor 9 Nm Running time motor 60 s Torque fail-safe 7 Nm Running time fail-safe 20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control Open/close Auxiliary switch 2x SPDT (5° / 80°) Cable 5 m Form fit 12x12 mm, continuous hollow shaft Manual override with position stop Direction of motion selectable by mounting L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Parts included Hand crank, Pointer, Protective bag Manufacturer Belimo Type BFN24/500
BKN230-24-MOD | Communication and power supply unit for fire damper actuators 24 V with connector Communication BACnet MS/TP, Modbus RTU with status LED Connection with power supply for a smoke switch Power supply AC 230 V
BKN230-24MP | Communication and power supply unit for fire damper actuators 24 V with connector Communication MP-Bus with status LED Connection with power supply for a smoke switch Power supply AC 230 V
BKN230-MOD | Communication and power supply unit for fire damper actuators 230 V Communication Modbus RTU with status LED Connection with power supply for a smoke switch Power supply AC 230 V
C215Q-F | 2-way Zone valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 1.2 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215Q-F
C215Q-J | 2-way Zone valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 4.8 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215Q-J
C215QFL-C | Pressure-independent 2-way flow limiter valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 290 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QFL-C
C215QFL-D | Pressure-independent 2-way flow limiter valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 470 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QFL-D
C215QFL-E | Pressure-independent 2-way flow limiter valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 650 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QFL-E
C215QFL-F | Pressure-independent 2-way flow limiter valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 1300 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QFL-F
C215QFL-F0 | Pressure-independent 2-way flow limiter valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 940 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QFL-F0
C215QP-B | Pressure-independent 2-way zone valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 0.058 l/s V'nom 210 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QP-B
C215QP-D | Pressure-independent 2-way zone valve DN 15, PN 25 Internal thread Rp 1/2" V'nom 0.117 l/s V'nom 420 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QP-D
C215QPT-B | Pressure-independent 2-way zone valve with measuring ports (P/T ports) DN 15, PN 25 Internal thread Rp 1/2" V'nom 0.058 l/s V'nom 210 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-B
C215QPT-B-11A | Piping package with pressure-independent 2-way zone valve DN 15, PN 25 Euro cone G 3/4" V'nom 210 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-B-11A
C215QPT-B-21A | Piping package with pressure-independent 2-way zone valve DN 15, PN 25 Euro cone G 3/4" V'nom 210 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-B-21A
C215QPT-D | Pressure-independent 2-way zone valve with measuring ports (P/T ports) DN 15, PN 25 Internal thread Rp 1/2" V'nom 0.117 l/s V'nom 420 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-D
C215QPT-D-11B | Piping package with pressure-independent 2-way zone valve DN 15, PN 25 Euro cone G 3/4" V'nom 420 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-D-11B
C215QPT-D-21B | Piping package with pressure-independent 2-way zone valve DN 15, PN 25 Euro cone G 3/4" V'nom 420 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPT-D-21B
C215QPW-N | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 15, PN 40 Internal thread Rp 1/2" Kvs 16 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C215QPW-N
C220Q-K | 2-way Zone valve DN 20, PN 25 Internal thread Rp 3/4" Kvs 8 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220Q-K
C220QFL-F6 | Pressure-independent 2-way flow limiter valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 1200 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QFL-F6
C220QFL-G | Pressure-independent 2-way flow limiter valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 1900 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QFL-G
C220QFL-G0 | Pressure-independent 2-way flow limiter valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 1500 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QFL-G0
C220QFL-H | Pressure-independent 2-way flow limiter valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 2900 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QFL-H
C220QFL-H0 | Pressure-independent 2-way flow limiter valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 2350 l/h Valve body Brass Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QFL-H0
C220QP-F | Pressure-independent 2-way zone valve DN 20, PN 25 Internal thread Rp 3/4" V'nom 0.272 l/s V'nom 980 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QP-F
C220QPT-F | Pressure-independent 2-way zone valve with measuring ports (P/T ports) DN 20, PN 25 Internal thread Rp 3/4" V'nom 0.272 l/s V'nom 980 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QPT-F
C220QPT-F-11CG | Piping package with pressure-independent 2-way zone valve DN 20, PN 25 Euro cone G 3/4" V'nom 980 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QPT-F-11CG
C220QPT-F-21C | Piping package with pressure-independent 2-way zone valve DN 20, PN 25 Euro cone G 3/4" V'nom 980 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QPT-F-21C
C220QPT-G-21D | Piping package with pressure-independent 2-way zone valve DN 20, PN 25 Euro cone G 3/4" V'nom 2100 l/h Differential pressure 16...350 kPa (PIQCV) Valve body Brass Fluid temperature 2...90°C [36...194°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C220QPT-G-21D
C225Q-K | 2-way Zone valve DN 25, PN 25 Internal thread Rp 1" Kvs 7 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C225Q-K
C225QPT-G | Pressure-independent 2-way zone valve with measuring ports (P/T ports) DN 25, PN 25 Internal thread Rp 1" V'nom 0.583 l/s V'nom 2100 l/h Differential pressure 16...350 kPa Valve body Brass Fluid temperature -20...120°C [-4...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C225QPT-G
C315Q-H | 3-way Changeover zone valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 2.5 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C315Q-H
C320Q-J | 3-way Changeover zone valve DN 20, PN 25 Internal thread Rp 3/4" Kvs 4 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C320Q-J
C325Q-J | 3-way Changeover zone valve DN 25, PN 25 Internal thread Rp 1" Kvs 4 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C325Q-J
C415Q-J | 2-way Zone valve DN 15, PN 25 External thread G 3/4" Kvs 4.5 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C415Q-J
C420Q-K | 2-way Zone valve DN 20, PN 25 External thread G 3/4" Kvs 7.8 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C420Q-K
C515Q-H | 3-way Changeover zone valve DN 15, PN 25 External thread G 3/4" Kvs 2.3 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C515Q-H
C520Q-J | 3-way Changeover zone valve DN 20, PN 25 External thread G 3/4" Kvs 3.6 m³/h Valve body Brass Fluid temperature 2...100°C [36...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type C520Q-J
C615QP-B+BAC | Pressure-independent 6-way zone valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 15, PN 16 Internal thread Rp 1/2" V'nom 210 l/h Valve body Nickel-plated brass body (6-way CCV) / Brass (PIQCV) Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Nominal voltage AC/DC 24 V Power consumption in operation 2.1 W Power consumption in rest position 1.9 W Power consumption for wire sizing 4.6 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type C615QP-B+BAC
C615QP-D+BAC | Pressure-independent 6-way zone valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 15, PN 16 Internal thread Rp 1/2" V'nom 420 l/h Valve body Nickel-plated brass body (6-way CCV) / Brass (PIQCV) Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Nominal voltage AC/DC 24 V Power consumption in operation 2.1 W Power consumption in rest position 1.9 W Power consumption for wire sizing 4.6 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type C615QP-D+BAC
C615QP-F+BAC | Pressure-independent 6-way zone valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 15, PN 16 Internal thread Rp 1/2" V'nom 980 l/h Valve body Nickel-plated brass body (6-way CCV) / Brass (PIQCV) Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Nominal voltage AC/DC 24 V Power consumption in operation 2.1 W Power consumption in rest position 1.9 W Power consumption for wire sizing 4.6 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type C615QP-F+BAC
C620QPT-G+BAC | Pressure-independent 6-way zone valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 20, PN 16 Internal thread Rp 3/4" V'nom 2100 l/h Valve body Nickel-plated brass body (6-way CCV) / Brass (PIQCV) Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Nominal voltage AC/DC 24 V Power consumption in operation 2.1 W Power consumption in rest position 1.9 W Power consumption for wire sizing 4.6 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type C620QPT-G+BAC
CH230-L100.2 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 380 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor by electrical installation Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CH230-L100.2
CH230-L60.2 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 380 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor by electrical installation Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CH230-L60.2
CH24-L100.2 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 380 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor by electrical installation Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-L100.2
CH24-L60.2 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 380 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor by electrical installation Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-L60.2
CH24-SR-L100.2 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 380 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor Y = 0 V: retracted Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-SR-L100.2
CH24-SR-L60.2 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 380 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor Y = 0 V: retracted Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-SR-L60.2
CH24-SR-R100.2 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 380 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor Y = 0 V: extended Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-SR-R100.2
CH24-SR-R60.2 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 125 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 380 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor Y = 0 V: extended Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CH24-SR-R60.2
CM230-F-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230-F-L
CM230-F-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230-F-R
CM230-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230-L
CM230-L-100D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 100 Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CM230-L-100D.2
CM230-L-125D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 125 Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CM230-L-125D.2
CM230-L-150D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 150 Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CM230-L-150D.2
CM230-L-160D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 160 Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Multipack 20 pcs. Manufacturer Belimo Type CM230-L-160D.2
CM230-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230-R
CM230G-F-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230G-F-L
CM230G-F-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230G-F-R
CM230G-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230G-L
CM230G-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CM230G-R
CM24-F-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-F-L
CM24-F-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-F-R
CM24-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-L
CM24-L-100D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 100 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-L-100D.2
CM24-L-125D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 125 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-L-125D.2
CM24-L-150D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 150 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-L-150D.2
CM24-L-160D.2 | Compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 160 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 58 s / 70° Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-L-160D.2
CM24-MPL-L | Communicative damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-MPL-L
CM24-MPL-R | Communicative damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-MPL-R
CM24-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-R
CM24-SR-F-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-F-L
CM24-SR-F-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-F-R
CM24-SR-F-T-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-F-T-L
CM24-SR-F-T-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-F-T-R
CM24-SR-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-L
CM24-SR-L-100D.2 | Modulating compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 100 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 58 s / 70° Operating range 2...10 V Position feedback 2...10 V Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-SR-L-100D.2
CM24-SR-L-125D.2 | Modulating compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 125 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 58 s / 70° Operating range 2...10 V Position feedback 2...10 V Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-SR-L-125D.2
CM24-SR-L-150D.2 | Modulating compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 150 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 58 s / 70° Operating range 2...10 V Position feedback 2...10 V Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-SR-L-150D.2
CM24-SR-L-160D.2 | Modulating compact actuator with damper blade Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Round duct diameter DN 160 Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 58 s / 70° Operating range 2...10 V Position feedback 2...10 V Angle of rotation 70° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24-SR-L-160D.2
CM24-SR-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-R
CM24-SR-T-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-T-L
CM24-SR-T-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SR-T-R
CM24-SX-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SX-L
CM24-SX-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SX-R
CM24-SX-T-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SX-T-L
CM24-SX-T-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-SX-T-R
CM24-T-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-T-L
CM24-T-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24-T-R
CM24G-F-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-F-L
CM24G-F-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-F-R
CM24G-L | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-L
CM24G-R | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-R
CM24G-SR-F-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-SR-F-L
CM24G-SR-F-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-SR-F-R
CM24G-SR-L | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-SR-L
CM24G-SR-R | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP66 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CM24G-SR-R
CM24K-F-T-L.2 | Damper actuator for module SKM230-T-B12 Current reduction in rest position Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage DC 24 V Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 95° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24K-F-T-L.2
CM24K-F-T-R.2 | Damper actuator for module SKM230-T-B12 Current reduction in rest position Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage DC 24 V Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 95° Manual override with magnet Mechanical interface Form fit 8x8 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24K-F-T-R.2
CM24K-T-L.2 | Damper actuator for module SKM230-T-B12 Current reduction in rest position Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage DC 24 V Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close Running time motor 75 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 95° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24K-T-L.2
CM24K-T-R.2 | Damper actuator for module SKM230-T-B12 Current reduction in rest position Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage DC 24 V Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close Running time motor 75 s / 90° Direction of motion motor clockwise rotation Angle of rotation 95° Manual override with magnet Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Terminals Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 20 pcs. Manufacturer Belimo Type CM24K-T-R.2
CMV-100-MP | VAV control unit CMV 2 Nm DN 100 AC/DC 24 V, modulating, communicative Communication MP-Bus Running time motor 70 s Operating range 2...10 V variable Feedback volume/position 2...10 V variable IP00, Manual override with magnet Electrical connection Cable 1 m PVC
CMV-125-MP | VAV control unit CMV 2 Nm DN 125 AC/DC 24 V, modulating, communicative Communication MP-Bus Running time motor 70 s Operating range 2...10 V variable Feedback volume/position 2...10 V variable IP00, Manual override with magnet Electrical connection Cable 1 m PVC
CMV-150-MP | VAV control unit CMV 2 Nm DN 150 AC/DC 24 V, modulating, communicative Communication MP-Bus Running time motor 70 s Operating range 2...10 V variable Feedback volume/position 2...10 V variable IP00, Manual override with magnet Electrical connection Cable 1 m PVC
CMV-160-MP | VAV control unit CMV 2 Nm DN 160 AC/DC 24 V, modulating, communicative Communication MP-Bus Running time motor 70 s Operating range 2...10 V variable Feedback volume/position 2...10 V variable IP00, Manual override with magnet Electrical connection Cable 1 m PVC
CQ230A | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.7 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQ230A
CQ230A-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.7 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQ230A-T
CQ24A | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.2 W Power consumption for wire sizing 0.6 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A
CQ24A-BAC | Communicative electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.7 W Power consumption in rest position 0.6 W Power consumption for wire sizing 1.5 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-BAC
CQ24A-MPL | Communicative electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.6 W Power consumption in rest position 0.4 W Power consumption for wire sizing 1.1 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-MPL
CQ24A-MPL-T | Communicative electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.6 W Power consumption in rest position 0.4 W Power consumption for wire sizing 1.1 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-MPL-T
CQ24A-SR | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 0.6 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-SR
CQ24A-SR-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 0.6 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-SR-T
CQ24A-SZ | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 0.6 VA Control modulating Running time motor 75 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-SZ
CQ24A-SZ-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 0.6 VA Control modulating Running time motor 75 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-SZ-T
CQ24A-SZ-T-LN | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.3 W Power consumption for wire sizing 0.6 VA Control modulating Running time motor 62 s / 74° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-SZ-T-LN
CQ24A-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.3 W Power consumption in rest position 0.2 W Power consumption for wire sizing 0.6 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQ24A-T
CQC230A | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.7 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 35 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQC230A
CQD230A | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.7 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 15 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQD230A
CQD24A | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 15 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A
CQD24A-MPL | Communicative electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 1.5 VA Control communicative Communication MP-Bus Running time motor 15 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-MPL
CQD24A-SR | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.3 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 15 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-SR
CQD24A-SR-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.3 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 15 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-SR-T
CQD24A-SZ | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.3 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 15 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-SZ
CQD24A-SZ-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.3 W Power consumption for wire sizing 1.5 VA Control modulating Running time motor 15 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-SZ-T
CQD24A-T | Electronic rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 15 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQD24A-T
CQK230A | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQK230A
CQK230A-T | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQK230A-T
CQK24A | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A
CQK24A-MPL | Communicative electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A-MPL
CQK24A-MPL-T | Communicative electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control communicative Communication MP-Bus Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A-MPL-T
CQK24A-SR | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control modulating Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A-SR
CQK24A-SR-T | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control modulating Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A-SR-T
CQK24A-T | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe 60 s / 90° Manual override with actuator (clicked out) Electrical connection Terminals PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQK24A-T
CQKD230A | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.5 W Power consumption for wire sizing 7 VA Control Open/close Running time motor 15 s / 90° Running time fail-safe 15 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type CQKD230A
CQKD24A | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 15 s / 90° Running time fail-safe 15 s / 90° Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQKD24A
CQKD24A-SR | Electronic fail-safe rotary actuator for zone valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Snap-assembly of the actuator Flow setting variable Deenergised closed (NC) Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control modulating Running time motor 15 s / 90° Running time fail-safe 15 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with actuator (clicked out) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type CQKD24A-SR
CR24-A1 | Room temperature controller with 1 sequence Output 2...10 V: VAV / cooling, heating (change over) AC 24 V without operating elements Terminals
CR24-A2 | Room temperature controller with 2 sequences Output 2...10 V: VAV / cooling Output 3-Point: heating AC 24 V without operating elements
CR24-A3 | Room temperature controller with 3 sequences Output 2...10 V: VAV Output 0...10 V: cooling, heating (change over) Output 3-Point: heating AC 24 V without operating elements
CR24-B1 | Room temperature controller with 1 sequence Output 2...10 V: VAV / cooling, heating (change over) AC 24 V Mode selection and display: AUTO / ECO / MAXIMUM, rotary button +/-
CR24-B2 | Room temperature controller with 2 sequences Output 2...10 V: VAV / cooling Output 3-Point: heating AC 24 V Mode selection and display: AUTO / ECO / MAXIMUM, rotary button +/-
CR24-B2E | Room temperature controller with manual operation Output 2...10 V: VAV / cooling Output 2x Triac: heating two-stage AC 24 V Mode selection and display: AUTO / ECO / MAXIMUM, rotary button +/-
CR24-B3 | Room temperature controller with 3 sequences Output 2...10 V: VAV Output 0...10 V: cooling, heating (change over) Output 3-Point: heating AC 24 V Mode selection and display: AUTO / ECO / MAXIMUM, rotary button +/-
CRA24-B1P | 3-step switch with button/LED Output 2...10 V: VAV AC 24 V Mode selection and display: COMF / MIN / MAX
CRA24-B3 | Room temperature controller with manual operation Output 2...10 V: supply air VAV Output 2...10 V: exhaust air VAV Output 2/3-Point: heating AC 24 V Mode selection and display: COMF / MIN / MAX, rotary button +/-
CRA24-B3P | Room temperature controller mode selection without button Output 2...10 V: supply air VAV Output 2...10 V: exhaust air VAV Output 2/3-Point: heating AC 24 V Mode selection and display: COMF / MIN / MAX
CRK24-B1 | Room temperature controller Output 2...10 V: cooling, heating for 6-way valve AC 24 V Mode selection and display: AUTO / ECO / MAXIMUM, rotary button +/-
CRP24-B1 | Positioner for wall mounting 0...100% operating range selectable 0...10 V or 2...10 V
CRZA-A | Spare cover for CR24-A.. controller without operating elements
CRZA-B | Spare cover for CR24-B.. controller Mode selection and rotary knob +/-
CRZW | Spare wall socket for CR24.. controller
D6100N | 2-way Butterfly valve with Wafer types DN 100, PN 6 / 10 / 16 Kvmax 520 m³/h Kvs 150 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6100N
D6100NL | 2-way Butterfly valve with Lug types DN 100, PN 10 / 16 Kvmax 520 m³/h Kvs 150 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6100NL
D6100W | 2-way Butterfly valve with Wafer types DN 100, PN 6 / 10 / 16 Kvmax 690 m³/h Kvs 220 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6100W
D6100WL | 2-way Butterfly valve with Lug types DN 100, PN 16 Kvmax 690 m³/h Kvs 220 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6100WL
D6125N | 2-way Butterfly valve with Wafer types DN 125, PN 6 / 10 / 16 Kvmax 880 m³/h Kvs 260 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6125N
D6125NL | 2-way Butterfly valve with Lug types DN 125, PN 10 / 16 Kvmax 880 m³/h Kvs 260 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6125NL
D6125W | 2-way Butterfly valve with Wafer types DN 125, PN 6 / 10 / 16 Kvmax 990 m³/h Kvs 310 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6125W
D6125WL | 2-way Butterfly valve with Lug types DN 125, PN 16 Kvmax 990 m³/h Kvs 310 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6125WL
D6150N | 2-way Butterfly valve with Wafer types DN 150, PN 6 / 10 / 16 Kvmax 1400 m³/h Kvs 400 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6150N
D6150NL | 2-way Butterfly valve with Lug types DN 150, PN 10 / 16 Kvmax 1400 m³/h Kvs 400 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6150NL
D6150W | 2-way Butterfly valve with Wafer types DN 150, PN 6 / 10 / 16 Kvmax 1780 m³/h Kvs 550 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6150W
D6150WL | 2-way Butterfly valve with Lug types DN 150, PN 16 Kvmax 1780 m³/h Kvs 550 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Closing element Stainless steel 1.4581 Fluid temperature -20...120°C [-4...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6150WL
D6200W | 2-way Butterfly valve with Wafer types DN 200, PN 6 / 10 / 16 Kvmax 2200 m³/h Kvs 820 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6200W
D6200WL | 2-way Butterfly valve with Lug types DN 200, PN 16 Kvmax 2200 m³/h Kvs 820 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6200WL
D6250W | 2-way Butterfly valve with Wafer types DN 250, PN 6 / 10 / 16 Kvmax 4200 m³/h Kvs 1300 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6250W
D6250WL | 2-way Butterfly valve with Lug types DN 250, PN 16 Kvmax 4200 m³/h Kvs 1300 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6250WL
D625N | 2-way Butterfly valve with Wafer types DN 25, PN 6 / 10 / 16 Kvmax 50 m³/h Kvs 24 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D625N
D625NL | 2-way Butterfly valve with Lug types DN 25, PN 10 / 16 Kvmax 50 m³/h Kvs 24 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D625NL
D6300W | 2-way Butterfly valve with Wafer types DN 300, PN 6 / 10 / 16 Kvmax 5700 m³/h Kvs 1740 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6300W
D6300WL | 2-way Butterfly valve with Lug types DN 300, PN 16 Kvmax 5700 m³/h Kvs 1740 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (CF-8, 1.4308) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6300WL
D632N | 2-way Butterfly valve with Wafer types DN 32, PN 6 / 10 / 16 Kvmax 55 m³/h Kvs 25 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D632N
D632NL | 2-way Butterfly valve with Lug types DN 32, PN 10 / 16 Kvmax 55 m³/h Kvs 25 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D632NL
D6350N | 2-way Butterfly valve with Wafer types DN 350, PN 10 / 16 Kvmax 10300 m³/h Kvs 3010 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6350N
D6350NL | 2-way Butterfly valve with Lug types DN 350, PN 16 Kvmax 10300 m³/h Kvs 3010 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6350NL
D6400N | 2-way Butterfly valve with Wafer types DN 400, PN 16 Kvmax 14200 m³/h Kvs 4140 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6400N
D6400NL | 2-way Butterfly valve with Lug types DN 400, PN 16 Kvmax 14200 m³/h Kvs 4140 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6400NL
D640N | 2-way Butterfly valve with Wafer types DN 40, PN 6 / 10 / 16 Kvmax 65 m³/h Kvs 27 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D640N
D640NL | 2-way Butterfly valve with Lug types DN 40, PN 10 / 16 Kvmax 65 m³/h Kvs 27 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D640NL
D6450N | 2-way Butterfly valve with Wafer types DN 450, PN 16 Kvmax 18800 m³/h Kvs 5490 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6450N
D6450NL | 2-way Butterfly valve with Lug types DN 450, PN 16 Kvmax 18800 m³/h Kvs 5490 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6450NL
D6500N | 2-way Butterfly valve with Wafer types DN 500, PN 16 Kvmax 24100 m³/h Kvs 7060 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6500N
D6500NL | 2-way Butterfly valve with Lug types DN 500, PN 16 Kvmax 24100 m³/h Kvs 7060 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6500NL
D650N | 2-way Butterfly valve with Wafer types DN 50, PN 6 / 10 / 16 Kvmax 100 m³/h Kvs 30 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D650N
D650NL | 2-way Butterfly valve with Lug types DN 50, PN 10 / 16 Kvmax 100 m³/h Kvs 30 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D650NL
D6600N | 2-way Butterfly valve with Wafer types DN 600, PN 16 Kvmax 37300 m³/h Kvs 10900 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6600N
D6600NL | 2-way Butterfly valve with Lug types DN 600, PN 16 Kvmax 37300 m³/h Kvs 10900 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6600NL
D665N | 2-way Butterfly valve with Wafer types DN 65, PN 6 / 10 / 16 Kvmax 170 m³/h Kvs 50 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D665N
D665NL | 2-way Butterfly valve with Lug types DN 65, PN 10 / 16 Kvmax 170 m³/h Kvs 50 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D665NL
D6700N | 2-way Butterfly valve with Wafer types DN 700, PN 16 Kvmax 42800 m³/h Kvs 11760 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6700N
D6700NL | 2-way Butterfly valve with Lug types DN 700, PN 16 Kvmax 42800 m³/h Kvs 11760 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D6700NL
D680N | 2-way Butterfly valve with Wafer types DN 80, PN 6 / 10 / 16 Kvmax 260 m³/h Kvs 75 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D680N
D680NL | 2-way Butterfly valve with Lug types DN 80, PN 10 / 16 Kvmax 260 m³/h Kvs 75 m³/h Valve body EN-GJS-400-15 (GGG 40) Closing element Stainless steel AISI 304 (1.4301) Fluid temperature -10...120°C [14...248°F] Leakage rate tight, leakage rate A Manufacturer Belimo Type D680NL
D7150NL/BAC | 2x D6150NL+ZPR01 2x PRCA-BAC-S2-T 3-way butterfly valve DN 150 Lug type, PN 16
D7200WL/BAC | 2x D6200WL+ZPR01 2x PRCA-BAC-S2-T-200 3-way butterfly valve DN 200 Lug type, PN 16
D7250WL/BAC | 2x D6250WL+ZPR01 2x PRCA-BAC-S2-T-250 3-way butterfly valve DN 250 Lug type, PN 16
D7300WL/BAC | 2x D6300WL+ZPR01 2x PRCA-BAC-S2-T 3-way butterfly valve DN 300 Lug type, PN 16
DR230A-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DR230A-5
DR230A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DR230A-7
DR230A-R | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DR230A-R
DR24A-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-5
DR24A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-7
DR24A-MP-5 | Communicative electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-MP-5
DR24A-MP-7 | Communicative electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-MP-7
DR24A-R | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-R
DR24A-SR-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-SR-5
DR24A-SR-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-SR-7
DR24A-TP-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DR24A-TP-7
DRC230A-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DRC230A-5
DRC230A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DRC230A-7
DRC230G-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DRC230G-5
DRC230G-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type DRC230G-7
DRC24A-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24A-5
DRC24A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24A-7
DRC24A-TP-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24A-TP-7
DRC24G-5 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24G-5
DRC24G-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24G-7
DRC24G-T-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 2 W Power consumption for wire sizing 12 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRC24G-T-7
DRK24A-5 | Electronic fail-safe rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 2 W Power consumption for wire sizing 20 VA Control Open/close Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRK24A-5
DRK24A-7 | Electronic fail-safe rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor Max. 90 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 2 W Power consumption for wire sizing 20 VA Control Open/close Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type DRK24A-7
EF230A | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 4.5 W Power consumption for wire sizing 21 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type EF230A
EF230A-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9 W Power consumption in rest position 4.5 W Power consumption for wire sizing 21 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type EF230A-S2
EF24A | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9.5 W Power consumption in rest position 4.5 W Power consumption for wire sizing 16 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A
EF24A-MF | Parametrisable fail-safe damper actuator Torque motor 30 Nm Running time motor 150 s Torque fail-safe 30 Nm Running time fail-safe <20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9.5 W Power consumption in rest position 4.5 W Power consumption for wire sizing 16 VA Control modulating Electrical connection Cable 1 m, with plug Universal shaft clamp 12...26.7 mm Manual override by means of hand crank and locking switch Direction of motion selectable with switch L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A-MF
EF24A-MP | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9.5 W Power consumption in rest position 4.5 W Power consumption for wire sizing 16 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A-MP
EF24A-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9.5 W Power consumption in rest position 4.5 W Power consumption for wire sizing 16 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A-S2
EF24A-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 4.5 W Power consumption for wire sizing 12 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A-SR
EF24A-SR-S2 | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 30 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 4.5 W Power consumption for wire sizing 12 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EF24A-SR-S2
EM-ECQ-02F | Belimo Energy Manifold Zones 2 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-02F
EM-ECQ-03F | Belimo Energy Manifold Zones 3 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-03F
EM-ECQ-04F | Belimo Energy Manifold Zones 4 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-04F
EM-ECQ-05F | Belimo Energy Manifold Zones 5 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-05F
EM-ECQ-06F | Belimo Energy Manifold Zones 6 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-06F
EM-ECQ-07F | Belimo Energy Manifold Zones 7 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-07F
EM-ECQ-08F | Belimo Energy Manifold Zones 8 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-08F
EM-ECQ-09F | Belimo Energy Manifold Zones 9 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-09F
EM-ECQ-10F | Belimo Energy Manifold Zones 10 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-10F
EM-ECQ-11F | Belimo Energy Manifold Zones 11 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-11F
EM-ECQ-12F | Belimo Energy Manifold Zones 12 Manifold Stainless steel Valve body Brass Fluid temperature 2...70°C [36...158°F] Manufacturer Belimo Type EM-ECQ-12F
EP015R-R6+BAC | Pressure-independent 6-way characterised control valve (EPIV) Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling With glycol compensation Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 15, PN 16 Internal thread Rp 1/2" V'nom 1260 l/h Nominal voltage AC/DC 24 V Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 5...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP015R-R6+BAC
EP015R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP015R2+BAC
EP015R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP015R2+KBAC
EP020R-R6+BAC | Pressure-independent 6-way characterised control valve (EPIV) Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling With glycol compensation Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App DN 20, PN 16 Internal thread Rp 3/4" V'nom 2340 l/h Nominal voltage AC/DC 24 V Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 5...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP020R-R6+BAC
EP020R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP020R2+BAC
EP020R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP020R2+KBAC
EP025R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP025R2+BAC
EP025R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP025R2+KBAC
EP032R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP032R2+BAC
EP032R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP032R2+KBAC
EP040R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP040R2+BAC
EP040R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP040R2+KBAC
EP050R2+BAC | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP050R2+BAC
EP050R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EP050R2+KBAC
EP065F+KMP | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Current reduction in rest position DN 65, PN 16 Flange V'nom 8 l/s Nominal voltage AC/DC 24 V Power consumption in operation 10 W Power consumption in rest position 5 W Power consumption for wire sizing 20 VA modulating, communicative Communication MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP065F+KMP
EP065F+MOD | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 65, PN 16 Flange V'nom 8 l/s Nominal voltage AC/DC 24 V Power consumption in operation 6 W Power consumption in rest position 4.5 W Power consumption for wire sizing 10 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP065F+MOD
EP065F+MP | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 65, PN 16 Flange V'nom 8 l/s Nominal voltage AC/DC 24 V Power consumption in operation 6 W Power consumption in rest position 4.5 W Power consumption for wire sizing 10 VA modulating, communicative Communication MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP065F+MP
EP080F+KMP | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Current reduction in rest position DN 80, PN 16 Flange V'nom 11 l/s Nominal voltage AC/DC 24 V Power consumption in operation 10 W Power consumption in rest position 5 W Power consumption for wire sizing 20 VA modulating, communicative Communication MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP080F+KMP
EP080F+MOD | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 80, PN 16 Flange V'nom 11 l/s Nominal voltage AC/DC 24 V Power consumption in operation 6 W Power consumption in rest position 4.5 W Power consumption for wire sizing 10 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP080F+MOD
EP080F+MP | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 80, PN 16 Flange V'nom 11 l/s Nominal voltage AC/DC 24 V Power consumption in operation 6 W Power consumption in rest position 4.5 W Power consumption for wire sizing 10 VA modulating, communicative Communication MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP080F+MP
EP100F+KMP | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Current reduction in rest position DN 100, PN 16 Flange V'nom 20 l/s Nominal voltage AC/DC 24 V Power consumption in operation 13 W Power consumption in rest position 7 W Power consumption for wire sizing 24 VA modulating, communicative Communication MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP100F+KMP
EP100F+MOD | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 100, PN 16 Flange V'nom 20 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP100F+MOD
EP100F+MP | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 100, PN 16 Flange V'nom 20 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative Communication MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP100F+MP
EP125F+KMP | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Current reduction in rest position DN 125, PN 16 Flange V'nom 31 l/s Nominal voltage AC/DC 24 V Power consumption in operation 13 W Power consumption in rest position 7 W Power consumption for wire sizing 24 VA modulating, communicative Communication MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP125F+KMP
EP125F+MOD | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 125, PN 16 Flange V'nom 31 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP125F+MOD
EP125F+MP | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 125, PN 16 Flange V'nom 31 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative Communication MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP125F+MP
EP150F+KMP | Pressure-independent 2-way characterised control valve with fail-safe (EPIV) Sensor-operated flow control Current reduction in rest position DN 150, PN 16 Flange V'nom 45 l/s Nominal voltage AC/DC 24 V Power consumption in operation 13 W Power consumption in rest position 7 W Power consumption for wire sizing 24 VA modulating, communicative Communication MP-Bus Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP150F+KMP
EP150F+MOD | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 150, PN 16 Flange V'nom 45 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP150F+MOD
EP150F+MP | Pressure-independent 2-way characterised control valve (EPIV) Sensor-operated flow control Current reduction in rest position DN 150, PN 16 Flange V'nom 45 l/s Nominal voltage AC/DC 24 V Power consumption in operation 9 W Power consumption in rest position 6 W Power consumption for wire sizing 12 VA modulating, communicative Communication MP-Bus V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EP150F+MP
EV015R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV015R2+BAC
EV015R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV015R2+KBAC
EV015R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV015R2+MID
EV015R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 15, PN 25 Internal and external thread Rp 1/2", G 3/4" V'nom 0.42 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV015R3+BAC
EV020R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV020R2+BAC
EV020R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV020R2+KBAC
EV020R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV020R2+MID
EV020R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 20, PN 25 Internal and external thread Rp 3/4", G 1" V'nom 0.69 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV020R3+BAC
EV025R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV025R2+BAC
EV025R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV025R2+KBAC
EV025R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV025R2+MID
EV025R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 25, PN 25 Internal and external thread Rp 1", G 1 1/4" V'nom 0.97 l/s Nominal voltage AC/DC 24 V Power consumption in operation 4 W Power consumption in rest position 3.7 W Power consumption for wire sizing 6.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV025R3+BAC
EV032R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV032R2+BAC
EV032R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV032R2+KBAC
EV032R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV032R2+MID
EV032R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 32, PN 25 Internal and external thread Rp 1 1/4", G 1 1/2" V'nom 1.67 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV032R3+BAC
EV040R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV040R2+BAC
EV040R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV040R2+KBAC
EV040R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV040R2+MID
EV040R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 40, PN 25 Internal and external thread Rp 1 1/2", G 2" V'nom 2.78 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV040R3+BAC
EV050R2+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV050R2+BAC
EV050R2+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 25...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV050R2+KBAC
EV050R2+MID | Pressure-independent 2-way characterised control valve (Energy Valve) Certification MID / EN 1434 Sensor-operated flow, power or differential pressure control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV050R2+MID
EV050R3+BAC | Pressure-independent 3-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Integrated delta T manager Data recording for 13 months Insulation shell included DN 50, PN 25 Internal and external thread Rp 2", G 2 1/2" V'nom 4.17 l/s Nominal voltage AC/DC 24 V Power consumption in operation 5 W Power consumption in rest position 3.9 W Power consumption for wire sizing 7.5 VA modulating, communicative, hybrid Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 25...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV050R3+BAC
EV065F+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 65, PN 16 Flange V'nom 8 l/s Nominal voltage AC/DC 24 V Power consumption in operation 7 W Power consumption in rest position 5 W Power consumption for wire sizing 6 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV065F+BAC
EV065F+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 65, PN 16 Flange V'nom 8 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15.5 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV065F+KBAC
EV080F+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 80, PN 16 Flange V'nom 11 l/s Nominal voltage AC/DC 24 V Power consumption in operation 7 W Power consumption in rest position 5 W Power consumption for wire sizing 6 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV080F+BAC
EV080F+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 80, PN 16 Flange V'nom 11 l/s Nominal voltage AC/DC 24 V Power consumption in operation 15.5 W Power consumption in rest position 6.5 W Power consumption for wire sizing 26 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV080F+KBAC
EV100F+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 100, PN 16 Flange V'nom 20 l/s Nominal voltage AC/DC 24 V Power consumption in operation 7 W Power consumption in rest position 5 W Power consumption for wire sizing 11 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV100F+BAC
EV100F+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 100, PN 16 Flange V'nom 20 l/s Nominal voltage AC/DC 24 V Power consumption in operation 16.5 W Power consumption in rest position 6.5 W Power consumption for wire sizing 29 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV100F+KBAC
EV125F+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 125, PN 16 Flange V'nom 31 l/s Nominal voltage AC/DC 24 V Power consumption in operation 7 W Power consumption in rest position 5 W Power consumption for wire sizing 11 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV125F+BAC
EV125F+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 125, PN 16 Flange V'nom 31 l/s Nominal voltage AC/DC 24 V Power consumption in operation 16.5 W Power consumption in rest position 6.5 W Power consumption for wire sizing 29 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV125F+KBAC
EV150F+BAC | Pressure-independent 2-way characterised control valve (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 150, PN 16 Flange V'nom 45 l/s Nominal voltage AC/DC 24 V Power consumption in operation 7 W Power consumption in rest position 5 W Power consumption for wire sizing 11 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud V'max adjustable 30...100% of V'nom Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV150F+BAC
EV150F+KBAC | Pressure-independent 2-way characterised control valve with fail-safe (Energy Valve) Sensor-operated flow or power control, power and energy monitoring function Glycol monitoring Current reduction in rest position Integrated delta T manager Data recording for 13 months DN 150, PN 16 Flange V'nom 45 l/s Nominal voltage AC/DC 24 V Power consumption in operation 16.5 W Power consumption in rest position 6.5 W Power consumption for wire sizing 29 VA modulating, communicative, hybrid, Cloud Communication BACnet/IP, BACnet MS/TP, Modbus TCP, Modbus RTU, MP-Bus, Cloud Running time fail-safe 35 s / 90° V'max adjustable 30...100% of V'nom Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type EV150F+KBAC
EV230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 1 W Power consumption for wire sizing 9.5 VA Control Open/close, 3-point Running time motor 150 s / 40 mm (188 s / 50 mm) Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type EV230A-RE
EV230A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 1 W Power consumption for wire sizing 9.5 VA Control Open/close, 3-point Running time motor 150 s / 40 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type EV230A-TPC
EV24A-MOD | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 40 mm Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-MOD
EV24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 40 mm (188 s / 50 mm) Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-MP-RE
EV24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 40 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-MP-TPC
EV24A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 40 mm (188 s / 50 mm) Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-RE
EV24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 40 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-SR-TPC
EV24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 40 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-SZ-TPC
EV24A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 40 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EV24A-TPC
EVC24A-MF | Parametrisable electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 1.5 W Power consumption for wire sizing 18 VA Control modulating ConfigurableShort MFT Running time motor 35 s / 40 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EVC24A-MF
EVC24A-MF-RE | Parametrisable electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 1.5 W Power consumption for wire sizing 18 VA Control modulating ConfigurableShort MFT Running time motor 35 s / 40 mm (44 s / 50 mm) Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EVC24A-MF-RE
EVC24A-SR | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 1.5 W Power consumption for wire sizing 18 VA Control modulating Running time motor 35 s / 40 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EVC24A-SR
EVC24A-SZ | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 2500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 1.5 W Power consumption for wire sizing 18 VA Control modulating Running time motor 35 s / 40 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type EVC24A-SZ
EXT-AC-2X-1M-TUBE | Tube for airflow volume probe Set of 2 pcs. 1000 mm
EXT-AC-2X-T-PCS444 | T-piece for airflow volume probe Set of 2 pcs.
EXT-AC-L200 | Airflow volume probe 200 mm min. 2 m/s
EXT-AC-L250 | Airflow volume probe 250 mm min. 2 m/s
EXT-AC-L300 | Airflow volume probe 300 mm min. 2 m/s
EXT-AC-L400 | Airflow volume probe 400 mm min. 2 m/s
EXT-AC-L500 | Airflow volume probe 500 mm min. 2 m/s
EXT-AC-L600 | Airflow volume probe 600 mm min. 2 m/s
EXT-AC-L700 | Airflow volume probe 700 mm min. 2 m/s
EXT-AC-R100 | Airflow volume probe 100 mm min. 2 m/s
EXT-AC-R125 | Airflow volume probe 125 mm min. 2 m/s
EXT-AC-R160 | Airflow volume probe 160 mm min. 2 m/s
EXT-AC-R200 | Airflow volume probe 200 mm min. 2 m/s
EXT-AC-R250 | Airflow volume probe 250 mm min. 2 m/s
EXT-AC-R315 | Airflow volume probe 315 mm min. 2 m/s
EXT-AC-R400 | Airflow volume probe 400 mm min. 2 m/s
EXT-AC-R500 | Airflow volume probe 500 mm min. 2 m/s
EXT-AC-R630 | Airflow volume probe 630 mm min. 2 m/s
EXT-EF-15A | MID accessory kit without fitting piece DN 15 Nickel-plated brass
EXT-EF-15B | MID accessory kit with fitting piece DN 15 Nickel-plated brass
EXT-EF-15C | MID accessory kit EV DN 15 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-15D | Pipe connector DN 15 Set of 2 pcs. Nickel-plated brass
EXT-EF-15E | MID accessory kit EV DN 15 Nickel-plated brass
EXT-EF-15F | Pipe connector DN 15 Nickel-plated brass
EXT-EF-15G | Open/close valve DN 15 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-20A | MID accessory kit without fitting piece DN 20 Nickel-plated brass
EXT-EF-20B | MID accessory kit with fitting piece DN 20 Nickel-plated brass
EXT-EF-20C | MID accessory kit EV DN 20 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-20D | Pipe connector DN 20 Set of 2 pcs. Nickel-plated brass
EXT-EF-20E | MID accessory kit EV DN 20 Nickel-plated brass
EXT-EF-20F | Pipe connector DN 20 Nickel-plated brass
EXT-EF-20G | Open/close valve DN 20 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-25A | MID accessory kit without fitting piece DN 25 Nickel-plated brass
EXT-EF-25B | MID accessory kit with fitting piece DN 25 Nickel-plated brass
EXT-EF-25C | MID accessory kit EV DN 25 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-25D | Pipe connector DN 25 Set of 2 pcs. Nickel-plated brass
EXT-EF-25E | MID accessory kit EV DN 25 Nickel-plated brass
EXT-EF-25F | Pipe connector DN 25 Nickel-plated brass
EXT-EF-25G | Open/close valve DN 25 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-32A | MID accessory kit without fitting piece DN 32 Nickel-plated brass
EXT-EF-32B | MID accessory kit with fitting piece DN 32 Nickel-plated brass
EXT-EF-32C | MID accessory kit EV DN 32 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-32D | Pipe connector DN 32 Set of 2 pcs. Nickel-plated brass
EXT-EF-32E | MID accessory kit EV DN 32 Nickel-plated brass
EXT-EF-32F | Pipe connector DN 32 Nickel-plated brass
EXT-EF-32G | Open/close valve DN 32 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-40A | MID accessory kit without fitting piece DN 40 Nickel-plated brass
EXT-EF-40B | MID accessory kit with fitting piece DN 40 Nickel-plated brass
EXT-EF-40C | MID accessory kit EV DN 40 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-40D | Pipe connector DN 40 Set of 2 pcs. Nickel-plated brass
EXT-EF-40E | MID accessory kit EV DN 40 Nickel-plated brass
EXT-EF-40F | Pipe connector DN 40 Nickel-plated brass
EXT-EF-40G | Open/close valve DN 40 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-50A | MID accessory kit without fitting piece DN 50 Nickel-plated brass
EXT-EF-50B | MID accessory kit with fitting piece DN 50 Nickel-plated brass
EXT-EF-50C | MID accessory kit EV DN 50 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-EF-50D | Pipe connector DN 50 Set of 2 pcs. Nickel-plated brass
EXT-EF-50E | MID accessory kit EV DN 50 Nickel-plated brass
EXT-EF-50F | Pipe connector DN 50 Nickel-plated brass
EXT-EF-50G | Open/close valve DN 50 For connecting and shutting off an Energy Valve MID Nickel-plated brass
EXT-H6100P-6500
EXT-H6100XP-6500
EXT-H6125P-8000
EXT-H6125XP-8000
EXT-H615P-125
EXT-H615P-200
EXT-H615XP-125
EXT-H615XP-200
EXT-H625P-315
EXT-H625P-400
EXT-H625XP-315
EXT-H625XP-400
EXT-H632P-650
EXT-H632XP-650
EXT-H640P-900
EXT-H640XP-900
EXT-H650P-1500
EXT-H650XP-1500
EXT-H665P-2500
EXT-H665XP-2500
EXT-H680P-3600
EXT-H680XP-3600
EXT-HL-15
EXT-HL-20
EXT-HL-25
EXT-J-00734645 | Safety temperature limiter STB switch Manual reset Output signal Switch Capillary 1 m Degree of protection IEC/EN IP54 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type EXT-J-00734645
EXT-J-00734647 | Safety temperature limiter STB switch Manual reset Output signal Switch Capillary 1 m Degree of protection IEC/EN IP54 Electrical connection Spring loaded terminal max. 2.5 mm² Manufacturer Belimo Type EXT-J-00734647
EXT-MR-249184 | Connecting cable 1.5 m for 22WP-.. / 22WDP-.. Cable
EXT-MR-249185 | Connecting cable 5 m for 22WP-.. / 22WDP-.. Cable
EXT-MU-ZRAB-P0-10
EXT-MU-ZRAB230-24
EXT-OC-ZQ15-P | Insulation shell for valve C2..QP-.. 2-way DN 15 only for non-condensing applications
EXT-OC-ZQ15-PT | Insulation shell for valve C2..QPT-.. 2-way DN 15 only for non-condensing applications
EXT-OC-ZQ20-P | Insulation shell for valve C2..QP-.. 2-way DN 20 only for non-condensing applications
EXT-OC-ZQ20-PT | Insulation shell for valve C2..QPT-.. 2-way DN 20 only for non-condensing applications
EXT-OC-ZQ25-PT | Insulation shell for valve C2..QPT-.. 2-way DN 25 only for non-condensing applications
EXT-OC-ZR-C215Q | Insulation shell for valve C2..Q-.. 2-way DN 15 only for non-condensing applications
EXT-OC-ZR-C220Q-K | Insulation shell for valve C2..Q-.. 2-way DN 20 only for non-condensing applications
EXT-OC-ZR-C225 | Insulation shell for valve C2..Q-.. 2-way DN 25 only for non-condensing applications
EXT-OC-ZR-C3015 | Insulation shell for valve R3015-..-..-B1 6-way DN 15 only for non-condensing applications
EXT-OC-ZR-C315Q-H | Insulation shell for valve C3..Q-.. 3-way DN 15 only for non-condensing applications
EXT-OC-ZR-C320Q-J | Insulation shell for valve C3..Q-.. 3-way DN 20 only for non-condensing applications
EXT-OC-ZR-C325 | Insulation shell for valve C3..Q-.. 3-way DN 25 only for non-condensing applications
EXT-OC-ZR-C4Q | Insulation shell for valve C4..Q-.. 2-way DN 15/20 only for non-condensing applications
EXT-OC-ZR-C5Q | Insulation shell for valve C5..Q-.. 3-way DN 15/20 only for non-condensing applications
EXT-OC-ZR3015 | Insulation shell for valve R30..-..-..-B2 6-way DN 15 only for non-condensing applications
EXT-OC-ZR3020 | Insulation shell for valve R30..-..-..-B2 6-way DN 20 only for non-condensing applications
EXT-OC-ZR3025 | Insulation shell for valve R30..-..-..-B3 6-way DN 25 only for non-condensing applications
EXT-OC-ZR415 | Insulation shell for valve R4.. 2-way DN 15 only for non-condensing applications
EXT-OC-ZR420 | Insulation shell for valve R4.. 2-way DN 20 only for non-condensing applications
EXT-OC-ZR425 | Insulation shell for valve R4.. 2-way DN 25 only for non-condensing applications
EXT-OC-ZR432 | Insulation shell for valve R4.. 2-way DN 32 only for non-condensing applications
EXT-OC-ZR440 | Insulation shell for valve R4.. 2-way DN 40 only for non-condensing applications
EXT-OC-ZR450 | Insulation shell for valve R4.. 2-way DN 50 only for non-condensing applications
EXT-OC-ZR515 | Insulation shell for valve R5.. 3-way DN 15 only for non-condensing applications
EXT-OC-ZR520 | Insulation shell for valve R5.. 3-way DN 20 only for non-condensing applications
EXT-OC-ZR525 | Insulation shell for valve R5.. 3-way DN 25 only for non-condensing applications
EXT-OC-ZR532 | Insulation shell for valve R5.. 3-way DN 32 only for non-condensing applications
EXT-OC-ZR540 | Insulation shell for valve R5.. 3-way DN 40 only for non-condensing applications
EXT-OC-ZR550 | Insulation shell for valve R5.. 3-way DN 50 only for non-condensing applications
EXT-OC-ZRN215 | Insulation shell for valve R2.. 2-way DN 15 (Kvs ≤1.6) only for non-condensing applications
EXT-OC-ZRN215G | Insulation shell for valve R2.. 2-way DN 15 (Kvs ≥2.5) only for non-condensing applications
EXT-OC-ZRN220 | Insulation shell for valve R2.. 2-way DN 20 only for non-condensing applications
EXT-OC-ZRN225 | Insulation shell for valve R2.. 2-way DN 25 only for non-condensing applications
EXT-OC-ZRN232 | Insulation shell for valve R2.. 2-way DN 32 only for non-condensing applications
EXT-OC-ZRN240 | Insulation shell for valve R2.. 2-way DN 40 only for non-condensing applications
EXT-OC-ZRN250 | Insulation shell for valve R2.. 2-way DN 50 only for non-condensing applications
EXT-OC-ZRN315 | Insulation shell for valve R3.. 3-way DN 15 (Kvs ≤1.6) only for non-condensing applications
EXT-OC-ZRN315G | Insulation shell for valve R3.. 3-way DN 15 (Kvs ≥2.5) only for non-condensing applications
EXT-OC-ZRN320 | Insulation shell for valve R3.. 3-way DN 20 only for non-condensing applications
EXT-OC-ZRN325 | Insulation shell for valve R3.. 3-way DN 25 only for non-condensing applications
EXT-OC-ZRN332 | Insulation shell for valve R3.. 3-way DN 32 only for non-condensing applications
EXT-OC-ZRN340 | Insulation shell for valve R3.. 3-way DN 40 (Kvs ≤16 / 31) only for non-condensing applications
EXT-OC-ZRN340G | Insulation shell for valve R3.. 3-way DN 40 (Kvs ≥25) only for non-condensing applications
EXT-OC-ZRN350 | Insulation shell for valve R3.. 3-way DN 50 (Kvs ≤25 / 49) only for non-condensing applications
EXT-OC-ZRN350G | Insulation shell for valve R3.. 3-way DN 50 (Kvs ≥40) only for non-condensing applications
EXT-SN-RBE05-S4-BE
EXT-SU-ZH4515M
EXT-SU-ZR4510M
EXT-SU-ZR4515M
EXT-SU-ZR4520M
EXT-SU-ZR4525M
EXT-SU-ZR4532M
EXT-SU-ZR4540M
EXT-SU-ZR4550M
EXT-SU-ZR4D15130F
EXT-SU-ZR4D20100F
EXT-SU-ZR4D20100G
EXT-SU-ZR4D20130F
EXT-SU-ZR4D20140F
EXT-SU-ZR4D20150F
EXT-SU-ZR4D25115F
EXT-SU-ZR4D25120G
EXT-SU-ZR4D25150F
EXT-SU-ZR4D25160F
EXT-SU-ZR4DK15100G
EXT-SU-ZR4DK15107G
EXT-SU-ZR4DK15130F
EXT-SU-ZR4DK1575F
EXT-SU-ZR4DK1580G
EXT-SU-ZR4DK2070G
EXT-SU-ZR4DK2075G
EXT-SUZR4D20100G25
EXT-SUZR4D20120G25
EXT-SUZR4D20160F25
EXT-SUZR4D25160F32
EXT-SUZR4D25180F32
EXT-SUZR4D25200F40
EXT-SUZR4DK15100G1
EXT-TT-1A | Open/close valve kit 1" angled 90° Brass CW 614 N
EXT-TT-1B | Open/close valve kit 1" straight Brass CW 614 N
EXT-TT-1C | Open/close valve kit for thermal energy meter 1" angled 90° Brass CW 614 N
EXT-TT-1D | Open/close valve kit for thermal energy meter 1" straight Brass CW 614 N
EXT-TT-1E | Open/close valve kit for thermal energy meter 3/4" straight Brass CW 614 N
EXT-TT-1F | Open/close valve kit for thermal energy meter 3/4" angled 90° Brass CW 614 N
EXT-WR-FP20-MP | FieldPower Box for MP-Bus IP20
EXT-ZR4D2080G1P25
EXT-ZR4D25109G1P5
FM065F-SZ | Flow sensor Ultrasonic volumetric flow measurement DN 65, PN 16 Nominal voltage AC/DC 24 V Flange FS 9.6 l/s Manufacturer Belimo Type FM065F-SZ
FM080F-SZ | Flow sensor Water PN 16 DN 80 Flow @ FS 13.6 l/s AC/DC 24 V, Voltage output 1 x 0...10 V, max. load 1 mA Ultrasonic volumetric flow measurement NEMA 2 / IP54
FM100F-SZ | Flow sensor Water PN 16 DN 100 Flow @ FS 24.0 l/s AC/DC 24 V, Voltage output 1 x 0...10 V, max. load 1 mA Ultrasonic volumetric flow measurement NEMA 2 / IP54
FM125F-SZ | Flow sensor Water PN 16 DN 125 Flow @ FS 37.5 l/s AC/DC 24 V, Voltage output 1 x 0...10 V, max. load 1 mA Ultrasonic volumetric flow measurement NEMA 2 / IP54
FM150F-SZ | Flow sensor Water PN 16 DN 150 Flow @ FS 54.0 l/s AC/DC 24 V, Voltage output 1 x 0...10 V, max. load 1 mA Ultrasonic volumetric flow measurement NEMA 2 / IP54
G-22PEM-A01 | Converter M-Bus
GK24A-1 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control Open/close Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-1
GK24A-MF | Parametrisable fail-safe damper actuator Torque motor 40 Nm Running time motor 150 s Running time fail-safe 35 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Electrical connection Cable 1 m, with plug Universal shaft clamp reversible 12...26.7 mm Manual override with push-button Direction of motion selectable with switch 0/1 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-MF
GK24A-MOD | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-MOD
GK24A-MP | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-MP
GK24A-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-SR
GK24A-SZ | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24A-SZ
GK24G-1 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control Open/close Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24G-1
GK24G-MP | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24G-MP
GK24G-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GK24G-SR
GM230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GM230A
GM230A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GM230A-TP
GM230G-T | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GM230G-T
GM24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A
GM24A-MF | Parametrisable damper actuator Torque motor 40 Nm Running time motor 150 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating Electrical connection Cable 1 m, with plug Universal shaft clamp reversible 12...26.7 mm Manual override with push-button, can be locked Direction of motion selectable with switch 0/1 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-MF
GM24A-MOD | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 5.5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-MOD
GM24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-MP
GM24A-MP-TP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-MP-TP
GM24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-SR
GM24A-SR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-SR-TP
GM24A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24A-TP
GM24G-MP-T | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24G-MP-T
GM24G-SR-T | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24G-SR-T
GM24G-T | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 14...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GM24G-T
GMC230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1 W Power consumption for wire sizing 11 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GMC230A
GR230A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GR230A-5
GR230A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GR230A-7
GR230A-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2 W Power consumption for wire sizing 9 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GR230A-R
GR24A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-5
GR24A-7 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-7
GR24A-MOD-5 | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-MOD-5
GR24A-MP-5 | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-MP-5
GR24A-MP-7 | Communicative electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-MP-7
GR24A-MP-R | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-MP-R
GR24A-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 2 W Power consumption for wire sizing 6 VA Control Open/close Running time motor 150 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-R
GR24A-SR-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-SR-5
GR24A-SR-7 | Modulating electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GR24A-SR-7
GRC230A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GRC230A-5
GRC230G-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GRC230G-5
GRC24A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2.5 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRC24A-5
GRC24G-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2.5 W Power consumption for wire sizing 11 VA Control Open/close Running time motor 35 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRC24G-5
GRC24G-MF-T-5 | Parametrisable electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2.5 W Power consumption for wire sizing 11 VA Control modulating ConfigurableShort MFT Running time motor 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRC24G-MF-T-5
GRC24G-SZ-T-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8 W Power consumption in rest position 2.5 W Power consumption for wire sizing 11 VA Control modulating Running time motor 35 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRC24G-SZ-T-5
GRK24A-5 | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control Open/close Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRK24A-5
GRK24A-SR-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRK24A-SR-5
GRK24A-SZ-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GRK24A-SZ-5
GV12-230-3-T | Electronic large globe valve actuator for large globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 15000 N Nominal voltage AC 230 V Nominal voltage frequency 50 Hz Power consumption for wire sizing 90 VA Control 3-point Auxiliary switch 2x SPDT Auxiliary switch note 0...100% Running time motor 82 s / 65 mm Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP65 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type GV12-230-3-T
GV12-24-SR-T | Electronic large globe valve actuator for large globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 15000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption for wire sizing 74 VA Control modulating Running time motor 82 s / 65 mm Operating range (0.5)2...10 V Position feedback 2...10 V Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP65 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type GV12-24-SR-T
H215S-G | 2-way Stainless steel globe valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 1.6 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H215S-G
H215S-J | 2-way Stainless steel globe valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 4.0 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H215S-J
H220S-K | 2-way Stainless steel globe valve DN 20, PN 25 Internal thread Rp 3/4" Kvs 6.3 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H220S-K
H225S-L | 2-way Stainless steel globe valve DN 25, PN 25 Internal thread Rp 1" Kvs 10 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H225S-L
H232S-M | 2-way Stainless steel globe valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 16 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H232S-M
H240S-N | 2-way Stainless steel globe valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 25 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H240S-N
H250S-P | 2-way Stainless steel globe valve DN 50, PN 25 Internal thread Rp 2" Kvs 40 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.01% of the Kvs value Manufacturer Belimo Type H250S-P
H315S-G | 3-way Stainless steel globe valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 1.6 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H315S-G
H315S-J | 3-way Stainless steel globe valve DN 15, PN 25 Internal thread Rp 1/2" Kvs 4.0 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H315S-J
H320S-K | 3-way Stainless steel globe valve DN 20, PN 25 Internal thread Rp 3/4" Kvs 6.3 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H320S-K
H325S-L | 3-way Stainless steel globe valve DN 25, PN 25 Internal thread Rp 1" Kvs 10 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H325S-L
H332S-M | 3-way Stainless steel globe valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 16 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H332S-M
H340S-N | 3-way Stainless steel globe valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 25 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H340S-N
H350S-P | 3-way Stainless steel globe valve DN 50, PN 25 Internal thread Rp 2" Kvs 40 m³/h Valve body Stainless steel AISI 304 Fluid temperature 0...130°C [32...266°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.02% of the Kvs value; B – AB: max. 0.02% of the Kvs value Manufacturer Belimo Type H350S-P
H411B | 2-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 0.63 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H411B
H412B | 2-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 1 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H412B
H413B | 2-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 1.6 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H413B
H414B | 2-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 2.5 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H414B
H415B | 2-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 4 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H415B
H420B | 2-way Globe valve DN 20, PN 16 External thread G 1 1/4" Kvs 6.3 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H420B
H425B | 2-way Globe valve DN 25, PN 16 External thread G 1 1/2" Kvs 10 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H425B
H432B | 2-way Globe valve DN 32, PN 16 External thread G 2" Kvs 16 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H432B
H440B | 2-way Globe valve DN 40, PN 16 External thread G 2 1/4" Kvs 25 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H440B
H450B | 2-way Globe valve DN 50, PN 16 External thread G 2 3/4" Kvs 40 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H450B
H511B | 3-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 0.63 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H511B
H512B | 3-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 1 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H512B
H513B | 3-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 1.6 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H513B
H514B | 3-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 2.5 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H514B
H515B | 3-way Globe valve DN 15, PN 16 External thread G 1 1/8" Kvs 4 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H515B
H520B | 3-way Globe valve DN 20, PN 16 External thread G 1 1/4" Kvs 6.3 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H520B
H525B | 3-way Globe valve DN 25, PN 16 External thread G 1 1/2" Kvs 10 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H525B
H532B | 3-way Globe valve DN 32, PN 16 External thread G 2" Kvs 16 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H532B
H540B | 3-way Globe valve DN 40, PN 16 External thread G 2 1/4" Kvs 25 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H540B
H550B | 3-way Globe valve DN 50, PN 16 External thread G 2 3/4" Kvs 40 m³/h Valve body CC499K Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H550B
H6015X1-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 1 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015X1-S2
H6015X1P6-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 1.6 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015X1P6-S2
H6015X2P5-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 2.5 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015X2P5-S2
H6015X4-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 4 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015X4-S2
H6015XP4-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 0.4 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015XP4-S2
H6015XP63-S2 | 2-way Globe valve DN 15, PN 25 Flange Kvs 0.63 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6015XP63-S2
H6020X4-S2 | 2-way Globe valve DN 20, PN 25 Flange Kvs 4 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6020X4-S2
H6020X6P3-S2 | 2-way Globe valve DN 20, PN 25 Flange Kvs 6.3 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6020X6P3-S2
H6025X10-S2 | 2-way Globe valve DN 25, PN 25 Flange Kvs 10 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6025X10-S2
H6025X6P3-S2 | 2-way Globe valve DN 25, PN 25 Flange Kvs 6.3 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6025X6P3-S2
H6032X10-S2 | 2-way Globe valve DN 32, PN 25 Flange Kvs 10 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6032X10-S2
H6032X16-S2 | 2-way Globe valve DN 32, PN 25 Flange Kvs 16 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6032X16-S2
H6040X16-S2 | 2-way Globe valve DN 40, PN 25 Flange Kvs 16 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6040X16-S2
H6040X25-S2 | 2-way Globe valve DN 40, PN 25 Flange Kvs 25 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6040X25-S2
H6050X25-S2 | 2-way Globe valve DN 50, PN 25 Flange Kvs 25 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6050X25-S2
H6050X40-S2 | 2-way Globe valve DN 50, PN 25 Flange Kvs 40 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6050X40-S2
H6065X58-SP2 | 2-way Globe valve (partial pressure-balanced) DN 65, PN 25 Flange Kvs 58 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6065X58-SP2
H6080X90-SP2 | 2-way Globe valve (partial pressure-balanced) DN 80, PN 25 Flange Kvs 90 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6080X90-SP2
H6100N | 2-way Globe valve DN 100, PN 16 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6100N
H6100R | 2-way Globe valve DN 100, PN 6 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6100R
H6100S | 2-way Globe valve DN 100, PN 16 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6100S
H6100SP | 2-way Globe valve (partial pressure-balanced) DN 100, PN 16 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6100SP
H6100X125-SP2 | 2-way Globe valve (partial pressure-balanced) DN 100, PN 25 Flange Kvs 125 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6100X125-SP2
H610S | 2-way Globe valve DN 15, PN 16 Flange Kvs 0.4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H610S
H611N | 2-way Globe valve DN 15, PN 16 Flange Kvs 0.63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H611N
H611R | 2-way Globe valve DN 15, PN 6 Flange Kvs 0.63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H611R
H611S | 2-way Globe valve DN 15, PN 16 Flange Kvs 0.63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H611S
H6125S | 2-way Globe valve DN 125, PN 16 Flange Kvs 220 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6125S
H6125SP | 2-way Globe valve (partial pressure-balanced) DN 125, PN 16 Flange Kvs 220 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6125SP
H612N | 2-way Globe valve DN 15, PN 16 Flange Kvs 1 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H612N
H612R | 2-way Globe valve DN 15, PN 6 Flange Kvs 1 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H612R
H612S | 2-way Globe valve DN 15, PN 16 Flange Kvs 1 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H612S
H613N | 2-way Globe valve DN 15, PN 16 Flange Kvs 1.6 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H613N
H613R | 2-way Globe valve DN 15, PN 6 Flange Kvs 1.6 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H613R
H613S | 2-way Globe valve DN 15, PN 16 Flange Kvs 1.6 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H613S
H614N | 2-way Globe valve DN 15, PN 16 Flange Kvs 2.5 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H614N
H614R | 2-way Globe valve DN 15, PN 6 Flange Kvs 2.5 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H614R
H614S | 2-way Globe valve DN 15, PN 16 Flange Kvs 2.5 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H614S
H6150S | 2-way Globe valve DN 150, PN 16 Flange Kvs 320 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6150S
H6150SP | 2-way Globe valve (partial pressure-balanced) DN 150, PN 16 Flange Kvs 320 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6150SP
H615N | 2-way Globe valve DN 15, PN 16 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H615N
H615R | 2-way Globe valve DN 15, PN 6 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H615R
H615S | 2-way Globe valve DN 15, PN 16 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H615S
H619S | 2-way Globe valve DN 20, PN 16 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H619S
H6200+GV12-230-3-T
H6200+GV12-24-SR-T
H6200W630-S7 | 2-way Globe valve DN 200, PN 16 Flange Kvs 630 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...120°C [41...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6200W630-S7
H620N | 2-way Globe valve DN 20, PN 16 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H620N
H620R | 2-way Globe valve DN 20, PN 6 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H620R
H620S | 2-way Globe valve DN 20, PN 16 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H620S
H624S | 2-way Globe valve DN 25, PN 16 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H624S
H6250+GV12-230-3-T
H6250+GV12-24-SR-T
H6250W1000-S7 | 2-way Globe valve DN 250, PN 16 Flange Kvs 1000 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...120°C [41...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H6250W1000-S7
H625N | 2-way Globe valve DN 25, PN 16 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H625N
H625R | 2-way Globe valve DN 25, PN 6 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H625R
H625S | 2-way Globe valve DN 25, PN 16 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H625S
H632N | 2-way Globe valve DN 32, PN 16 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H632N
H632R | 2-way Globe valve DN 32, PN 6 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H632R
H632S | 2-way Globe valve DN 32, PN 16 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H632S
H640N | 2-way Globe valve DN 40, PN 16 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H640N
H640R | 2-way Globe valve DN 40, PN 6 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H640R
H640S | 2-way Globe valve DN 40, PN 16 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H640S
H640SP | 2-way Globe valve (partial pressure-balanced) DN 40, PN 16 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H640SP
H650N | 2-way Globe valve DN 50, PN 16 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H650N
H650R | 2-way Globe valve DN 50, PN 6 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H650R
H650S | 2-way Globe valve DN 50, PN 16 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H650S
H650SP | 2-way Globe valve (partial pressure-balanced) DN 50, PN 16 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H650SP
H664N | 2-way Globe valve DN 65, PN 16 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H664N
H664R | 2-way Globe valve DN 65, PN 6 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H664R
H664S | 2-way Globe valve DN 65, PN 16 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H664S
H664SP | 2-way Globe valve (partial pressure-balanced) DN 65, PN 16 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H664SP
H665N | 2-way Globe valve DN 65, PN 16 Flange Kvs 63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H665N
H665S | 2-way Globe valve DN 65, PN 16 Flange Kvs 63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H665S
H679N | 2-way Globe valve DN 80, PN 16 Flange Kvs 90 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H679N
H679R | 2-way Globe valve DN 80, PN 6 Flange Kvs 90 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H679R
H679SP | 2-way Globe valve (partial pressure-balanced) DN 80, PN 16 Flange Kvs 90 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H679SP
H680N | 2-way Globe valve DN 80, PN 16 Flange Kvs 100 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H680N
H680S | 2-way Globe valve DN 80, PN 16 Flange Kvs 100 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve equal percentage Leakage rate Leakage rate max. 0.05% of the Kvs value Manufacturer Belimo Type H680S
H7015X4-S2 | 3-way Globe valve DN 15, PN 25 Flange Kvs 4 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7015X4-S2
H7020X6P3-S2 | 3-way Globe valve DN 20, PN 25 Flange Kvs 6.3 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7020X6P3-S2
H7025X10-S2 | 3-way Globe valve DN 25, PN 25 Flange Kvs 10 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7025X10-S2
H7032X16-S2 | 3-way Globe valve DN 32, PN 25 Flange Kvs 16 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7032X16-S2
H7040X25-S2 | 3-way Globe valve DN 40, PN 25 Flange Kvs 25 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7040X25-S2
H7050X40-S2 | 3-way Globe valve DN 50, PN 25 Flange Kvs 40 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7050X40-S2
H7065X63-S4 | 3-way Globe valve DN 65, PN 25 Flange Kvs 63 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7065X63-S4
H7080X100-S4 | 3-way Globe valve DN 80, PN 25 Flange Kvs 100 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7080X100-S4
H7100N | 3-way Globe valve DN 100, PN 16 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7100N
H7100R | 3-way Globe valve DN 100, PN 6 Flange Kvs 145 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7100R
H7100S | 3-way Globe valve DN 100, PN 16 Flange Kvs 160 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7100S
H7100X160-S4 | 3-way Globe valve DN 100, PN 25 Flange Kvs 160 m³/h Valve body EN-GJS-400-18-LT (GGG 40.3) Fluid temperature 5...200°C [41...392°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7100X160-S4
H711N | 3-way Globe valve DN 15, PN 16 Flange Kvs 0.63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H711N
H711R | 3-way Globe valve DN 15, PN 6 Flange Kvs 0.63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H711R
H7125N | 3-way Globe valve DN 125, PN 16 Flange Kvs 220 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7125N
H7125S | 3-way Globe valve DN 125, PN 16 Flange Kvs 220 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7125S
H712N | 3-way Globe valve DN 15, PN 16 Flange Kvs 1 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H712N
H712R | 3-way Globe valve DN 15, PN 6 Flange Kvs 1 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H712R
H713N | 3-way Globe valve DN 15, PN 16 Flange Kvs 1.6 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H713N
H713R | 3-way Globe valve DN 15, PN 6 Flange Kvs 1.6 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H713R
H714N | 3-way Globe valve DN 15, PN 16 Flange Kvs 2.5 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H714N
H714R | 3-way Globe valve DN 15, PN 6 Flange Kvs 2.5 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H714R
H7150N | 3-way Globe valve DN 150, PN 16 Flange Kvs 320 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7150N
H7150S | 3-way Globe valve DN 150, PN 16 Flange Kvs 320 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7150S
H715N | 3-way Globe valve DN 15, PN 16 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H715N
H715R | 3-way Globe valve DN 15, PN 6 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H715R
H715S | 3-way Globe valve DN 15, PN 16 Flange Kvs 4 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H715S
H7200+GV12-230-3-T
H7200+GV12-24-SR-T
H7200W630-S7 | 3-way Globe valve DN 200, PN 16 Flange Kvs 630 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7200W630-S7
H720N | 3-way Globe valve DN 20, PN 16 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H720N
H720R | 3-way Globe valve DN 20, PN 6 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H720R
H720S | 3-way Globe valve DN 20, PN 16 Flange Kvs 6.3 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H720S
H7250+GV12-230-3-T
H7250+GV12-24-SR-T
H7250W1000-S7 | 3-way Globe valve DN 250, PN 16 Flange Kvs 1000 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: linear; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H7250W1000-S7
H725N | 3-way Globe valve DN 25, PN 16 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H725N
H725R | 3-way Globe valve DN 25, PN 6 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H725R
H725S | 3-way Globe valve DN 25, PN 16 Flange Kvs 10 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H725S
H732N | 3-way Globe valve DN 32, PN 16 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H732N
H732R | 3-way Globe valve DN 32, PN 6 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H732R
H732S | 3-way Globe valve DN 32, PN 16 Flange Kvs 16 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H732S
H740N | 3-way Globe valve DN 40, PN 16 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H740N
H740R | 3-way Globe valve DN 40, PN 6 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H740R
H740S | 3-way Globe valve DN 40, PN 16 Flange Kvs 25 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H740S
H750N | 3-way Globe valve DN 50, PN 16 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H750N
H750R | 3-way Globe valve DN 50, PN 6 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H750R
H750S | 3-way Globe valve DN 50, PN 16 Flange Kvs 40 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H750S
H764N | 3-way Globe valve DN 65, PN 16 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H764N
H764R | 3-way Globe valve DN 65, PN 6 Flange Kvs 58 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H764R
H765N | 3-way Globe valve DN 65, PN 16 Flange Kvs 63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H765N
H765S | 3-way Globe valve DN 65, PN 16 Flange Kvs 63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H765S
H779N | 3-way Globe valve DN 80, PN 16 Flange Kvs 90 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H779N
H779R | 3-way Globe valve DN 80, PN 6 Flange Kvs 90 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H779R
H780N | 3-way Globe valve DN 80, PN 16 Flange Kvs 100 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H780N
H780S | 3-way Globe valve DN 80, PN 16 Flange Kvs 100 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature 5...150°C [41...302°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate Leakage rate A – AB: max. 0.05% of the Kvs value; B – AB: max. 1% of the Kvs value Manufacturer Belimo Type H780S
HH230 | Heater with mechanical humidistat
HH230-FG | Heater with mechanical humidistat
HH230-MG | Heater with mechanical humidistat
HH24-FG | Heater with mechanical humidistat
HH24-MG | Heater with mechanical humidistat
HR230-3 | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HR230-3
HR230-3-S | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 140 s / 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HR230-3-S
HR24-3 | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HR24-3
HR24-3-S | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 140 s / 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HR24-3-S
HR24-SR | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 90° Operating range 2...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 2...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HR24-SR
HRY24-SR | Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption for wire sizing 4 VA Control modulating Running time motor 35 s / 90° Operating range 0...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HRY24-SR
HT230 | Heater with adjustable thermostat
HT230-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HT230-3
HT230-3-S | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HT230-3-S
HT230-3-T | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HT230-3-T
HT230-FG | Heater with adjustable thermostat
HT230-MG | Heater with adjustable thermostat
HT24-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HT24-3
HT24-3-S | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HT24-3-S
HT24-3-T | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HT24-3-T
HT24-FG | Heater with adjustable thermostat
HT24-MG | Heater with adjustable thermostat
HT24-SR | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 90° Operating range 2...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HT24-SR
HT24-SR-T | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 90° Operating range 2...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HT24-SR-T
HTC230-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 70 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HTC230-3
HTC24-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 70 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTC24-3
HTC24-SR | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 70 s / 90° Operating range 0...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 0...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTC24-SR
HTD230-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption for wire sizing 2.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HTD230-3
HTD24-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTD24-3
HTD24-SR | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 90° Operating range 2...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTD24-SR
HTL230-3-T | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption for wire sizing 2.5 VA Control 3-point Running time motor 280 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HTL230-3-T
HTL24-3-T | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 280 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTL24-3-T
HTY24-SR | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption for wire sizing 4 VA Control modulating Running time motor 35 s / 90° Operating range 0...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 0...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTY24-SR
HTYD230-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 35 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type HTYD230-3
HTYD24-3 | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 35 s / 90° Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTYD24-3
HTYD24-SR | Electronic rotary actuator for mixing valves Current reduction in rest position Constant, load-independent running time Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 0...10 V Operating range selectable 0...10 V or 2...10 V Position feedback 0...10 V Direction of motion motor clockwise rotation Angle of rotation 90° Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type HTYD24-SR
IND-AFB | End stop indicator for NF..A / SF..A Galvanised steel
IND-EFB | End stop indicator for EF..A Galvanised steel
JRCA-BAC-S2-T | Electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 90 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 7 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 55 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type JRCA-BAC-S2-T
JRCA-S2-T | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 90 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 7 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 55 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type JRCA-S2-T
K-ELA | Shaft clamp one-sided for LM..A, TM..A clamping range ø6...20 mm Multipack 20 pcs.
K-ELA10 | Shaft clamp one-sided for LM..A, TM..A clamping range ø6...10 mm Multipack 20 pcs.
K-ELA13 | Shaft clamp one-sided for LM..A, TM..A clamping range ø6...13 mm Multipack 20 pcs.
K-ELA16 | Shaft clamp one-sided for LM..A, TM..A clamping range ø6...16 mm Multipack 20 pcs.
K-ENMA | Shaft clamp one-sided for NM..A clamping range ø8...26 mm with insert Multipack 20 pcs.
K-ENSA | Shaft clamp one-sided for NM..A, SM..A clamping range ø8...26 mm Multipack 20 pcs.
K-ENSA-I | Shaft clamp one-sided for SM..A for CrNi (INOX) clamping range ø12...26 mm for CrNi shaft (INOX) Multipack 20 pcs.
K-NA | Shaft clamp reversible for NM..A, LMQ..A clamping range ø8...20 mm
K-SA | Shaft clamp reversible for SM..A, NKQ..A, NMQ..A clamping range ø10...20 mm
K5A | Shaft clamp for TM/LM..A..-F.. with form fit 8x8 mm clamping range ø8...12 mm
K6-1 | Shaft clamp reversible for LF.. clamping range ø16...20 mm
K7-2 | Shaft clamp reversible for NF..A / SF..A for central mounting for damper shafts ø12.7 / 19.0 / 25.4 mm
K7-3 | Shaft clamp reversible for NF..A / SF..A clamping range ø10...20 mm
K9-2 | Shaft clamp reversible for EF..A clamping range ø12...26.7 mm
KG10A | Ball joint suitable for damper crank arm KH8 / KH10 for round iron rods with ø10 mm
KG10A.2 | Ball joint suitable for damper crank arm KH8 / KH10 for round iron rods with ø10 mm Multipack 20 pcs.
KG8 | Ball joint suitable for damper crank arm KH8 for round iron rods with ø8 mm
KG8.2 | Ball joint suitable for damper crank arm KH8 for round iron rods with ø8 mm Multipack 20 pcs.
KH-AFB | Actuator arm Die cast zinc Galvanised steel for NF..A / SF..A for 3/4" shafts clamping range ø10...22 mm Slot width 8.2 mm
KH-EFB | Actuator arm Galvanised steel Slot width 8.2 mm for EF..A
KH-LF | Actuator arm Galvanised steel for LF.. clamping range ø8...16 mm Slot width 8.2 mm
KH10 | Damper crank arm Galvanised steel Slot width 8.2 mm clamping range ø14...25 mm
KH8 | Damper crank arm Galvanised steel Slot width 8.2 mm clamping range ø10...18 mm
KR230 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 1 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type KR230
KR24 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 75 s / 90° Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type KR24
KR24-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control modulating Running time motor 75 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with magnet Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type KR24-SR
LF230 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LF230
LF230-S | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LF230-S
LF24 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24
LF24-3 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5 VA Control 3-point Running time motor 150 s / 90° Running time fail-safe <20 s Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24-3
LF24-MFT2 | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24-MFT2
LF24-S | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24-S
LF24-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24-SR
LF24-VST | VAV-Universal fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control communicative PP Running time motor 120 s / 90° Running time fail-safe <20 s / 90° Manual override No Mechanical interface Universal shaft clamp 8...16 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LF24-VST
LH230A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230A100
LH230A200 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230A200
LH230A300 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230A300
LH230A60 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230A60
LH230ASR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230ASR100
LH230ASR200 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 200 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LH230ASR200
LH24A-MOD200 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MOD200
LH24A-MP100 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP100
LH24A-MP100-TP | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP100-TP
LH24A-MP200 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP200
LH24A-MP200-TP | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP200-TP
LH24A-MP300 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP300
LH24A-MP300-TP | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP300-TP
LH24A-MP60-TP | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-MP60-TP
LH24A-SR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-SR100
LH24A-SR200 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 200 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-SR200
LH24A-SX60 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.9 W Power consumption for wire sizing 3 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A-SX60
LH24A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A100
LH24A200 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A200
LH24A300 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A300
LH24A60 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LH24A60
LHQ24A-MF100 | Parametrisable linear actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 100 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating ConfigurableShort MFT Running time motor 3.5 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LHQ24A-MF100
LHQ24A-SR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 100 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 3.5 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LHQ24A-SR100
LHQ24A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 100 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 3.5 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LHQ24A100
LHV-D3-KNX | VAV-Compact device – with VAV controller, dynamic Δp sensor and linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control communicative Communication KNX (S-Mode) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LHV-D3-KNX
LHV-D3-MOD | VAV-Compact device – with VAV controller, dynamic Δp sensor and linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LHV-D3-MOD
LHV-D3-MP | VAV-Compact device – with VAV controller, dynamic Δp sensor and linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Actuating force motor 150 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LHV-D3-MP
LM230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230A
LM230A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230A-F
LM230A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230A-S
LM230A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230A-S-TP
LM230A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230A-TP
LM230ASR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230ASR
LM230ASR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM230ASR-TP
LM24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A
LM24A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-F
LM24A-KNX | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control communicative Communication KNX (S-Mode) Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-KNX
LM24A-MOD | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-MOD
LM24A-MOD-J6 | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Connector socket RJ12 Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-MOD-J6
LM24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-MP
LM24A-MP-TP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-MP-TP
LM24A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-S
LM24A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-S-TP
LM24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-SR
LM24A-SR-F | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-SR-F
LM24A-SR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-SR-TP
LM24A-SX | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-SX
LM24A-SX-F | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-SX-F
LM24A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-TP
LM24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.4 W Power consumption for wire sizing 2 VA Control communicative PP Running time motor 120 s / 90° Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24A-VST
LM24AP5 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.2 W Power consumption for wire sizing 1.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Feedback potentiometer 5 kΩ Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LM24AP5
LM72A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage DC 48...110 V Power consumption in operation 2.5 W Power consumption in rest position 2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM72A
LM72A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage DC 48...110 V Power consumption in operation 2.5 W Power consumption in rest position 2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM72A-S
LM72A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage DC 48...110 V Power consumption in operation 2.5 W Power consumption in rest position 2 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LM72A-SR
LMC230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LMC230A
LMC230A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LMC230A-F
LMC230A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LMC230A-S
LMC24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMC24A
LMC24A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMC24A-F
LMC24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMC24A-SR
LMC24A-SR-F | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMC24A-SR-F
LMQ24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 2.5 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMQ24A
LMQ24A-MF | Parametrisable damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating ConfigurableShort MFT Running time motor 2.5 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMQ24A-MF
LMQ24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 2.5 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMQ24A-SR
LMQ24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control communicative PP Running time motor 2.5 s / 90° Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LMQ24A-VST
LMV-D3-KNX | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control communicative Communication KNX (S-Mode) Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LMV-D3-KNX
LMV-D3-MOD | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LMV-D3-MOD
LMV-D3-MP | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LMV-D3-MP
LMV-M1-MOD | VAV-Compact device – with VAV controller, static Δp sensor (membrane) and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LMV-M1-MOD
LMV-M1-MP | VAV-Compact device – with VAV controller, static Δp sensor (membrane) and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type LMV-M1-MP
LR230A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LR230A
LR230A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LR230A-S
LR230A-TP | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LR230A-TP
LR24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A
LR24A-KNX | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control communicative Communication KNX (S-Mode) Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-KNX
LR24A-MOD | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-MOD
LR24A-MOD-J6 | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Connector socket RJ12 Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-MOD-J6
LR24A-MP | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.3 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-MP
LR24A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-S
LR24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-SR
LR24A-SR-TP | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-SR-TP
LR24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 90 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-SZ
LR24A-TP | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LR24A-TP
LRC24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRC24A-SR
LRC24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRC24A-SZ
LRD230A | Rotary actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Running time motor 15 s Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 6.5 VA Control Open/close, 3-point Electrical connection Cable 1 m Manual override with push-button, can be locked Direction of motion Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LRD230A
LRF230 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LRF230
LRF230-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LRF230-O
LRF230-S | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 85° Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LRF230-S
LRF230-S-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 4 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2 W Power consumption for wire sizing 6.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 85° Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LRF230-S-O
LRF24 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24
LRF24-MP | Communicative electronic fail-safe rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Deenergised closed (NC) Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 10 VA Control modulating, communicative Communication MP-Bus Running time motor 75 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-MP
LRF24-MP-O | Communicative electronic fail-safe rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Deenergised open (NO) Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 10 VA Control modulating, communicative Communication MP-Bus Running time motor 75 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-MP-O
LRF24-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-O
LRF24-S | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 85° Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-S
LRF24-S-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 85° Running time motor 75 s / 90° Running time fail-safe <20 s Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-S-O
LRF24-SR | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override with hand crank, can be fixed in any position Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRF24-SR
LRQ24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 9 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRQ24A
LRQ24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 9 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRQ24A-SR
LRQ24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 4 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 9 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LRQ24A-SZ
LV230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 200 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LV230A-RE
LV230A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 15 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type LV230A-TPC
LV24A-MOD | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 15 mm Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-MOD
LV24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative Communication MP-Bus Running time motor 200 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-MP-RE
LV24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 15 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-MP-TPC
LV24A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 200 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-RE
LV24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 15 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-SR-TPC
LV24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control modulating Running time motor 150 s / 15 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-SZ-TPC
LV24A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 1 VA Control Open/close, 3-point Running time motor 150 s / 15 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LV24A-TPC
LVC24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 3.5 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 15 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LVC24A-MP-TPC
LVC24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control modulating Running time motor 35 s / 15 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LVC24A-SR-TPC
LVC24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3.5 VA Control modulating Running time motor 35 s / 15 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type LVC24A-SZ-TPC
MFT-C | Adapter for Service-Tool ZTH easy Connection with quick release terminals Parametrisation of actuators with ZTH EU or PC-Tool
MFT-P | Belimo PC-Tool Software for adjustments and diagnostics for MF/MP/MOD/LON/KNX actuators incl. fire protection CD with Software and instructions (de/en) for Windows operating systems
MS-NMAE | Mounting kit for NM..A actuators for mixing valves with 12 mm round shaft
MS-NRA | Mounting kit for NR/HT actuators for LK mixing valve
MS-NRB | Mounting kit for NR/HT actuators for Barberi mixing valves
MS-NRC | Mounting kit for NR/HT actuators for Honeywell/Centra DR..MA mixing valves
MS-NRC1 | Mounting kit for NR/HT actuators for Honeywell/Centra DRU.. mixing valves
MS-NRD | Mounting kit for NR/HT actuators for Danfoss valves HRB, HRE
MS-NRE | Mounting kit for NR/HT actuators for mixing valves with 12 mm round shaft
MS-NRE1 | Mounting kit for NR/HT actuators for ESBE mixing valves 3MG(A)/MGR/4HG and Thermomix mixing valves D15S..D32S
MS-NRE2 | Mounting kit for NR/HT actuators for Thermomix mixing valves D15...D32
MS-NRE3 | Mounting kit for NR/HT actuators for ESBE mixing valves 4MG(A) and Thermomix mixing valves C15S..C32S
MS-NRE4 | Mounting kit for NR/HT actuators for Thermomix mixing valves C15...C32
MS-NRE6 | Mounting kit for NR/HT actuators for ESBE mixing valves VRG/VRB/VRH
MS-NRH | Mounting kit for NR/HT actuators for Hora mixing valves
MS-NRL | Mounting kit for NR/HT actuators for Siemens/Landis&Stäfa mixing valves VCI/VBG/VBF
MS-NRL1 | Mounting kit for NR/HT actuators for Siemens/Landis&Stäfa mixing valves VBI
MS-NRLA | Mounting kit for NR/HT actuators for Lazzari mixing valves
MS-NRLO | Mounting kit for NR/HT actuators for Lovato mixing valves
MS-NRO1 | Mounting kit for NR/HT actuators for Meibes mixing valves
MS-NRS | Mounting kit for NR/HT actuators for Satchwell MB mixing valves
MS-NRSF | Mounting kit for NR/HT actuators for Satchwell MBF mixing valves
NF24A | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A
NF24A-3 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9 VA Control 3-point Running time motor 150 s / 90° Running time fail-safe <20 s Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-3
NF24A-MOD | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 9.5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-MOD
NF24A-MP | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 9.5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-MP
NF24A-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-S2
NF24A-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-SR
NF24A-SR-S2 | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-SR-S2
NF24A-SZ | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-SZ
NF24A-SZ-S2 | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-SZ-S2
NF24A-VST | VAV-Universal fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8 VA Control communicative PP Running time motor 120 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24A-VST
NF24G-MP-L | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 8 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24G-MP-L
NF24G-SR-L | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24G-SR-L
NF24G-SR-S2-L | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 5.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NF24G-SR-S2-L
NFA | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NFA
NFA-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NFA-S2
NFG-L | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NFG-L
NFG-S2-L | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NFG-S2-L
NKQ24A-1 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control Open/close Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24A-1
NKQ24A-MF | Parametrisable fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control modulating ConfigurableShort MFT Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24A-MF
NKQ24A-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control modulating Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24A-SR
NKQ24A-SZ | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control modulating Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24A-SZ
NKQ24A-VST | VAV-Universal fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control communicative PP Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Manual override with push-button Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24A-VST
NKQ24P-1 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control Open/close Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24P-1
NKQ24P-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 6 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 22 VA Control modulating Running time motor 4 s / 90° Running time fail-safe 4 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NKQ24P-SR
NM230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230A
NM230A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230A-F
NM230A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230A-S
NM230A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230A-S-TP
NM230A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230A-TP
NM230ASR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230ASR
NM230ASR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230ASR-TP
NM230P | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230P
NM230P-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230P-S
NM230PSR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NM230PSR
NM24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A
NM24A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-F
NM24A-KNX | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control communicative Communication KNX (S-Mode) Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-KNX
NM24A-MOD | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-MOD
NM24A-MOD-J6 | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Connector socket RJ12 Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-MOD-J6
NM24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-MP
NM24A-MP-TP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-MP-TP
NM24A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-S
NM24A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-S-TP
NM24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-SR
NM24A-SR-F | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-SR-F
NM24A-SR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-SR-TP
NM24A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-TP
NM24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control communicative PP Running time motor 120 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-VST
NM24A-VST-RE | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control communicative PP Running time motor 120 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24A-VST-RE
NM24AP5 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Feedback potentiometer 5 kΩ Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24AP5
NM24P | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24P
NM24P-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24P-MP
NM24P-P5 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Running time motor 150 s / 90° Feedback potentiometer 5 kΩ Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24P-P5
NM24P-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 3.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24P-S
NM24P-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NM24P-SR
NMC24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMC24A-MP
NMD230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 20 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NMD230A
NMQ24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 4 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMQ24A
NMQ24A-MF | Parametrisable damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating ConfigurableShort MFT Running time motor 4 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMQ24A-MF
NMQ24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 4 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMQ24A-SR
NMQ24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control communicative PP Running time motor 4 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMQ24A-VST
NMQ24A-VST-RE | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control communicative PP Running time motor 4 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NMQ24A-VST-RE
NMV-D3-KNX | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control communicative Communication KNX (S-Mode) Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-D3-KNX
NMV-D3-MOD | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-D3-MOD
NMV-D3-MP | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-D3-MP
NMV-D3-RE | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-D3-RE
NMV-D3-RE2-SET
NMV-M1-MOD | VAV-Compact device – with VAV controller, static Δp sensor (membrane) and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-M1-MOD
NMV-M1-MP | VAV-Compact device – with VAV controller, static Δp sensor (membrane) and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type NMV-M1-MP
NR230A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NR230A
NR230A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NR230A-S
NR24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A
NR24A-KNX | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 6 VA Control communicative Communication KNX (S-Mode) Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-KNX
NR24A-MOD | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-MOD
NR24A-MOD-J6 | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Connector socket RJ12 Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-MOD-J6
NR24A-MP | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-MP
NR24A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-S
NR24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-SR
NR24A-SR-TP | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-SR-TP
NR24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NR24A-SZ
NRC24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRC24A-SR
NRC24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 35 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRC24A-SZ
NRD230-3-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRD230-3-SI
NRD24-3-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRD24-3-SI
NRD24-SR-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRD24-SR-SI
NRDVX230-3-T-CA | Electronic short stroke actuator for Cazzaniga short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRDVX230-3-T-CA
NRDVX230-3-T-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRDVX230-3-T-SI
NRDVX24-3-T-CA | Electronic short stroke actuator for Cazzaniga short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRDVX24-3-T-CA
NRDVX24-3-T-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 1.5 VA Control 3-point Running time motor 140 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRDVX24-3-T-SI
NRDVX24-SR-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRDVX24-SR-SI
NRDVX24-SR-T-CA | Modulating electronic short stroke actuator for Cazzaniga short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 5.5 mm Operating range 2...10 V Position feedback 2...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRDVX24-SR-T-CA
NRDVX24-SR-T-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 140 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRDVX24-SR-T-SI
NRF230A-3 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 3 W Power consumption for wire sizing 15 VA Control 3-point Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRF230A-3
NRF230A-3-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 3 W Power consumption for wire sizing 15 VA Control 3-point Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRF230A-3-O
NRF230A-3-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 3 W Power consumption for wire sizing 15 VA Control 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRF230A-3-S2
NRF230A-3-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 3 W Power consumption for wire sizing 15 VA Control 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRF230A-3-S2-O
NRF24A | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A
NRF24A-MP | Communicative electronic fail-safe rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Deenergised closed (NC) Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 9.5 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-MP
NRF24A-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-O
NRF24A-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-S2
NRF24A-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 8.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-S2-O
NRF24A-SR | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SR
NRF24A-SR-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SR-O
NRF24A-SR-S2 | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SR-S2
NRF24A-SR-S2-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SR-S2-O
NRF24A-SZ | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SZ
NRF24A-SZ-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SZ-O
NRF24A-SZ-S2 | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 6 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRF24A-SZ-S2
NRFA | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFA
NRFA-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFA-O
NRFA-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFA-S2
NRFA-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 10 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 2.5 W Power consumption for wire sizing 9.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFA-S2-O
NRFD230A-3 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 16 VA Control 3-point Running time motor 35 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFD230A-3
NRFD230A-3-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 16 VA Control 3-point Running time motor 35 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFD230A-3-O
NRFD230A-3-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 16 VA Control 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 35 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFD230A-3-S2
NRFD230A-3-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 16 VA Control 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 35 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (A – AB = 0%) Manual override No Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRFD230A-3-S2-O
NRQ24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 9 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRQ24A
NRQ24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 9 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRQ24A-SR
NRQ24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 8 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 9 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRQ24A-SZ
NRYC24-SR-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 17 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRYC24-SR-SI
NRYD230-3-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption for wire sizing 3.5 VA Control 3-point Running time motor 35 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NRYD230-3-SI
NRYD24-3-SI | Electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 400 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 3 VA Control 3-point Running time motor 35 s / 5.5 mm Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRYD24-3-SI
NRYD24-SR-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRYD24-SR-SI
NRYDVX24-SR-T-SI | Modulating electronic short stroke actuator for Siemens short stroke globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 35 s / 5.5 mm Operating range 0...10 V Position feedback 0...10 V Manual override temporary and permanent gear train disengagement with rotary knob on the housing Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NRYDVX24-SR-T-SI
NV230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NV230A-RE
NV230A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NV230A-TPC
NV24A-MOD | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-MOD
NV24A-MOD-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-MOD-RE
NV24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-MP-RE
NV24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-MP-TPC
NV24A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-RE
NV24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 150 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-SR-TPC
NV24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-SZ-TPC
NV24A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NV24A-TPC
NVC230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 6.5 VA Control Open/close, 3-point Running time motor 35 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NVC230A-RE
NVC230A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 6.5 VA Control Open/close, 3-point Running time motor 35 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NVC230A-TPC
NVC24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5.5 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-MP-RE
NVC24A-MP-SZ-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5.5 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Operating range 0.5...10 V variable Position feedback 0.5...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-MP-SZ-RE
NVC24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5.5 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-MP-TPC
NVC24A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control Open/close, 3-point Running time motor 35 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-RE
NVC24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5.5 VA Control modulating Running time motor 35 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-SR-TPC
NVC24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5.5 VA Control modulating Running time motor 35 s / 20 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVC24A-SZ-TPC
NVK230A-3 | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control 3-point Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NVK230A-3
NVK230A-3-RE | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4.5 VA Control 3-point Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type NVK230A-3-RE
NVK24A-3-RE | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control 3-point Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Manual override with push-button Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-3-RE
NVK24A-3-TPC | Electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1000 N Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control 3-point Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-3-TPC
NVK24A-MOD | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Manual override with push-button Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-MOD
NVK24A-MP-RE | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-MP-RE
NVK24A-MP-TPC | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-MP-TPC
NVK24A-SR-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-SR-TPC
NVK24A-SZ-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVK24A-SZ-TPC
NVKC24A-MP-RE | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 9 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVKC24A-MP-RE
NVKC24A-MP-TPC | Communicative electronic fail-safe globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 9 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVKC24A-MP-TPC
NVKC24A-SR-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 9 VA Control modulating Running time motor 35 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVKC24A-SR-TPC
NVKC24A-SZ-TPC | Modulating electronic fail-safe globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 9 VA Control modulating Running time motor 35 s / 20 mm Running time fail-safe 35 s / 20 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type NVKC24A-SZ-TPC
P-01RT-1B-0 | Room Operating Unit Temperature passive Output signal Pt1000 Potentiometer 0.7...1.3 kOhm Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type P-01RT-1B-0
P-01RT-1F-0 | Room Operating Unit Temperature passive Output signal NTC1k8 Potentiometer 0.7...1.3 kOhm Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type P-01RT-1F-0
P-01RT-1L-0 | Room Operating Unit Temperature passive Output signal NTC10k (10k2) Potentiometer 2.5...8.5 kOhm Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type P-01RT-1L-0
P-01RT-1M-0 | Room Operating Unit Temperature passive Output signal NTC10k Pre (10k3) Potentiometer 2.5...8.5 kOhm Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.5...1.5 mm² Manufacturer Belimo Type P-01RT-1M-0
P-22RT-1800D-1 | Room Operating Unit Temperature active NFC Display type ePaper touch display Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, 0...20 mA, MP-Bus Measured values Temperature Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RT-1800D-1
P-22RT-1900D-1 | Room Operating Unit Temperature active NFC Display type ePaper touch display Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RT-1900D-1
P-22RTH-1800D-1 | Room Operating Unit Humidity / Temperature NFC Display type ePaper touch display Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, 0...20 mA, MP-Bus Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTH-1800D-1
P-22RTH-1900A-1 | Room Operating Unit Humidity / Temperature NFC Display type Belimo Display App Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTH-1900A-1
P-22RTH-1900D-1 | Room Operating Unit Humidity / Temperature NFC Display type ePaper touch display Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTH-1900D-1
P-22RTH-1U00A-2 | Room sensor Humidity / Temperature NFC Display type Belimo Display App Nominal voltage AC/DC 24 V Output signal Modbus, BACnet Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTH-1U00A-2
P-22RTH-1U00D-2 | Room Operating Unit Humidity / Temperature NFC Display type ePaper touch display Nominal voltage AC/DC 24 V Output signal Modbus, BACnet Measured values Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTH-1U00D-2
P-22RTM-1800D-1 | Room Operating Unit CO₂ / Humidity / Temperature NFC Display type ePaper touch display and LED Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, 0...20 mA, MP-Bus Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTM-1800D-1
P-22RTM-1900A-1 | Room Operating Unit CO₂ / Humidity / Temperature NFC Display type Belimo Display App and LED Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTM-1900A-1
P-22RTM-1900D-1 | Room Operating Unit CO₂ / Humidity / Temperature NFC Display type ePaper touch display and LED Nominal voltage AC/DC 24 V Output signal 0...5 V, 0...10 V, 2...10 V, MP-Bus Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTM-1900D-1
P-22RTM-1U00A-2 | Room sensor CO₂ / Humidity / Temperature NFC Display type Belimo Display App and LED Nominal voltage AC/DC 24 V Output signal Modbus, BACnet Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTM-1U00A-2
P-22RTM-1U00D-2 | Room Operating Unit CO₂ / Humidity / Temperature NFC Display type ePaper touch display and LED Nominal voltage AC/DC 24 V Output signal Modbus, BACnet Measured values CO₂, Temperature, Humidity Degree of protection IEC/EN IP30 Electrical connection Spring loaded terminal 0.25...1.5 mm² Manufacturer Belimo Type P-22RTM-1U00D-2
P10000A | Feedback potentiometer add-on 10 kΩ Cable 1 m FRNC
P10000A GR | Feedback potentiometer add-on, grey 10 kΩ Cable 1 m FRNC
P1000A | Feedback potentiometer add-on 1 kΩ Cable 1 m FRNC
P1000A GR | Feedback potentiometer add-on, grey 1 kΩ Cable 1 m FRNC
P1000A-F | Feedback potentiometer LF, NF..A, SF..A, BLF, BF, NF-US, AF-US 1 kΩ incl. installation accessories Cable 1 m FRNC
P140A | Feedback potentiometer add-on 140 Ω Cable 1 m FRNC
P140A GR | Feedback potentiometer add-on, grey 140 Ω Cable 1 m FRNC
P200A
P200A-F
P2800A
P2800A GR
P2P15PE-1GE | Elbow 90° male/female DN 15 Set of 2 pcs. Nickel-plated brass
P2P20PF-1GE | Elbow 90° male/female DN 20 Set of 2 pcs. Nickel-plated brass
P2P25PE-1GE | Elbow 90° male/female DN 25 Set of 2 pcs. Nickel-plated brass
P5000A
P5000A GR
P500A
P500A GR
PKCA-BAC-S2-T | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 52 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 54 VA / with 240 V 68 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Running time fail-safe 30 s / 90° Direction of motion motor electronically reversible Angle of rotation Max. 95° Manual override hand lever Mechanical interface Form fit 17x17 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PKCA-BAC-S2-T
PMCA-BAC-S2-T | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 19 VA / with 240 V 49 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Direction of motion motor electronically reversible Angle of rotation Max. 95° Manual override hand lever Mechanical interface Form fit 17x17 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PMCA-BAC-S2-T
PMCA-S2-T | Damper actuator Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 19 VA / with 240 V 49 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° Running time motor 35 s / 90° Direction of motion motor electronically reversible Angle of rotation Max. 95° Manual override hand lever Mechanical interface Form fit 17x17 mm Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PMCA-S2-T
PRCA-BAC-S2-T | Electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-BAC-S2-T
PRCA-BAC-S2-T-200 | Electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-BAC-S2-T-200
PRCA-BAC-S2-T-250 | Electronic rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-BAC-S2-T-250
PRCA-S2-T | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-S2-T
PRCA-S2-T-200 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-S2-T-200
PRCA-S2-T-250 | Electronic rotary actuator for butterfly valves Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 20 W Power consumption in rest position 6 W Power consumption for wire sizing with 24 V 20 VA / with 240 V 52 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Running time motor 35 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRCA-S2-T-250
PRKCA-BAC-S2-T | Electronic fail-safe rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 52 W Power consumption in rest position 9 W Power consumption for wire sizing with 24 V 54 VA / with 240 V 68 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Running time fail-safe 30 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRKCA-BAC-S2-T
PRKCA-BAC-S2-T-200 | Electronic fail-safe rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 52 W Power consumption in rest position 9 W Power consumption for wire sizing with 24 V 54 VA / with 240 V 68 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Running time fail-safe 30 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRKCA-BAC-S2-T-200
PRKCA-BAC-S2-T-250 | Electronic fail-safe rotary actuator for butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Integrated smart heater prevents condensation in the actuator Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 160 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 52 W Power consumption in rest position 9 W Power consumption for wire sizing with 24 V 54 VA / with 240 V 68 VA Control modulating, communicative, hybrid Auxiliary switch 2x SPDT Auxiliary switch note 1x 10° / 1x 0...90° (default setting 85°) Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Running time fail-safe 30 s / 90° Manual override hand crank Electrical connection Terminals Degree of protection IEC/EN IP66/67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type PRKCA-BAC-S2-T-250
R-22PE-0UC | Accessories Ultrasonic volumetric flow measurement DN 15, PN 25 Nominal voltage AC/DC 24 V External thread, G 3/4" qp 1.5 m³/h Manufacturer Belimo Type R-22PE-0UC
R-22PE-0UD | Accessories Ultrasonic volumetric flow measurement DN 20, PN 25 Nominal voltage AC/DC 24 V External thread, G 1" qp 2.5 m³/h Manufacturer Belimo Type R-22PE-0UD
R-22PE-0UE | Accessories Ultrasonic volumetric flow measurement DN 25, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/4" qp 3.5 m³/h Manufacturer Belimo Type R-22PE-0UE
R-22PE-0UF | Accessories Ultrasonic volumetric flow measurement DN 32, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/2" qp 6 m³/h Manufacturer Belimo Type R-22PE-0UF
R-22PE-0UG | Accessories Ultrasonic volumetric flow measurement DN 40, PN 25 Nominal voltage AC/DC 24 V External thread, G 2" qp 10 m³/h Manufacturer Belimo Type R-22PE-0UG
R-22PE-0UH | Accessories Ultrasonic volumetric flow measurement DN 50, PN 25 Nominal voltage AC/DC 24 V External thread, G 2 1/2" qp 15 m³/h Manufacturer Belimo Type R-22PE-0UH
R-22PEM-0UC | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 15, PN 25 Nominal voltage AC/DC 24 V External thread, G 3/4" qp 1.5 m³/h Manufacturer Belimo Type R-22PEM-0UC
R-22PEM-0UD | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 20, PN 25 Nominal voltage AC/DC 24 V External thread, G 1" qp 2.5 m³/h Manufacturer Belimo Type R-22PEM-0UD
R-22PEM-0UE | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 25, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/4" qp 3.5 m³/h Manufacturer Belimo Type R-22PEM-0UE
R-22PEM-0UF | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 32, PN 25 Nominal voltage AC/DC 24 V External thread, G 1 1/2" qp 6 m³/h Manufacturer Belimo Type R-22PEM-0UF
R-22PEM-0UG | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 40, PN 25 Nominal voltage AC/DC 24 V External thread, G 2" qp 10 m³/h Manufacturer Belimo Type R-22PEM-0UG
R-22PEM-0UH | Accessories MID / EN 1434 Ultrasonic volumetric flow measurement DN 50, PN 25 Nominal voltage AC/DC 24 V External thread, G 2 1/2" qp 15 m³/h Manufacturer Belimo Type R-22PEM-0UH
R2015-1-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 1 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-1-S1
R2015-1P6-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-1P6-S1
R2015-2P5-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-2P5-S1
R2015-4-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-4-S1
R2015-6P3-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-6P3-S1
R2015-P25-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-P25-S1
R2015-P4-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-P4-S1
R2015-P63-S1 | 2-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-P63-S1
R2015-S1 | 2-way Open/close ball valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 15 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2015-S1
R2020-4-S2 | 2-way Characterised control valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2020-4-S2
R2020-6P3-S2 | 2-way Characterised control valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2020-6P3-S2
R2020-8P6-S2 | 2-way Characterised control valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 8.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2020-8P6-S2
R2020-S2 | 2-way Open/close ball valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2020-S2
R2025-10-S2 | 2-way Characterised control valve DN 25, PN 40 Internal thread Rp 1" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2025-10-S2
R2025-16-S2 | 2-way Characterised control valve DN 25, PN 40 Internal thread Rp 1" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2025-16-S2
R2025-6P3-S2 | 2-way Characterised control valve DN 25, PN 40 Internal thread Rp 1" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2025-6P3-S2
R2025-S2 | 2-way Open/close ball valve DN 25, PN 40 Internal thread Rp 1" Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2025-S2
R2032-16-S3 | 2-way Characterised control valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2032-16-S3
R2032-S3 | 2-way Open/close ball valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2032-S3
R2040-16-S3 | 2-way Characterised control valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2040-16-S3
R2040-25-S3 | 2-way Characterised control valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2040-25-S3
R2040-S3 | 2-way Open/close ball valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 31 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2040-S3
R2050-25-S4 | 2-way Characterised control valve DN 50, PN 25 Internal thread Rp 2" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2050-25-S4
R2050-40-S4 | 2-way Characterised control valve DN 50, PN 25 Internal thread Rp 2" Kvs 40 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2050-40-S4
R2050-S4 | 2-way Open/close ball valve DN 50, PN 25 Internal thread Rp 2" Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R2050-S4
R215PW-N | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 15, PN 40 Internal thread Rp 1/2" Kvs 16 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R215PW-N
R220PW-P | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 20, PN 40 Internal thread Rp 3/4" Kvs 32 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R220PW-P
R225FL-J | Pressure-independent 2-way flow limiter valve DN 25, PN 25 Internal thread Rp 1" V'nom 3600 l/h Valve body Nickel-plated brass body Fluid temperature 2...60°C [36...140°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R225FL-J
R225PW-Q | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 25, PN 40 Internal thread Rp 1" Kvs 40 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R225PW-Q
R232PW-Q | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 63 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R232PW-Q
R240PW-R | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 100 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R240PW-R
R250PW-S | 2-way Open/close ball valve Potable water certificate: ACS, DVGW, WRAS, ÜA DN 50, PN 25 Internal thread Rp 2" Kvs 150 m³/h Valve body Lead free and dezincification resistant (ISO 6509) brass (CW511L) Fluid temperature 5...100°C [41...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R250PW-S
R3015-1-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-1-B2
R3015-1-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-1P3-B2
R3015-1-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-1P8-B2
R3015-1-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-P25-B2
R3015-1-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-P4-B2
R3015-1-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1-P63-B2
R3015-1-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 1 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-1-S1
R3015-1P3-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-1-B2
R3015-1P3-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-1P3-B2
R3015-1P3-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-1P8-B2
R3015-1P3-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-P25-B2
R3015-1P3-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-P4-B2
R3015-1P3-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.3 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P3-P63-B2
R3015-1P6-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-1P6-S1
R3015-1P8-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-1-B2
R3015-1P8-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-1P3-B2
R3015-1P8-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-1P8-B2
R3015-1P8-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-P25-B2
R3015-1P8-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-P4-B2
R3015-1P8-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 1.8 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-1P8-P63-B2
R3015-2P5-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-2P5-S1
R3015-4-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-4-S1
R3015-BL1 | 3-way Changeover ball valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 5.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-BL1
R3015-P25-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-1-B2
R3015-P25-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-1P3-B2
R3015-P25-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-1P8-B2
R3015-P25-P25-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P25-B1
R3015-P25-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P25-B2
R3015-P25-P4-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P4-B1
R3015-P25-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P4-B2
R3015-P25-P63-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P63-B1
R3015-P25-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.25 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P25-P63-B2
R3015-P25-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-P25-S1
R3015-P4-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-1-B2
R3015-P4-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-1P3-B2
R3015-P4-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-1P8-B2
R3015-P4-P25-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P25-B1
R3015-P4-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P25-B2
R3015-P4-P4-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P4-B1
R3015-P4-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P4-B2
R3015-P4-P63-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P63-B1
R3015-P4-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.4 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P4-P63-B2
R3015-P4-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-P4-S1
R3015-P63-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-1-B2
R3015-P63-1P3-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 1.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-1P3-B2
R3015-P63-1P8-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 1.8 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-1P8-B2
R3015-P63-P25-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P25-B1
R3015-P63-P25-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.25 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P25-B2
R3015-P63-P4-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P4-B1
R3015-P63-P4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P4-B2
R3015-P63-P63-B1 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Brass Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P63-B1
R3015-P63-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 15, PN 16 Internal thread Rp 1/2" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3015-P63-P63-B2
R3015-P63-S1 | 3-way Characterised control valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3015-P63-S1
R3015-S1 | 3-way Changeover ball valve DN 15, PN 40 Internal thread Rp 1/2" Kvs 15 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3015-S1
R3020-1-1P6-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1-1P6-B2
R3020-1-2P5-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1-2P5-B2
R3020-1-4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1 m³/h Kvs (Sequence 2) 4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1-4-B2
R3020-1P6-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1.6 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1P6-1-B2
R3020-1P6-1P6-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1.6 m³/h Kvs (Sequence 2) 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1P6-1P6-B2
R3020-1P6-2P5-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1.6 m³/h Kvs (Sequence 2) 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1P6-2P5-B2
R3020-1P6-4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1.6 m³/h Kvs (Sequence 2) 4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1P6-4-B2
R3020-1P6-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 1.6 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-1P6-P63-B2
R3020-2P5-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 2.5 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-2P5-1-B2
R3020-2P5-1P6-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 2.5 m³/h Kvs (Sequence 2) 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-2P5-1P6-B2
R3020-2P5-2P5-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 2.5 m³/h Kvs (Sequence 2) 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-2P5-2P5-B2
R3020-2P5-4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 2.5 m³/h Kvs (Sequence 2) 4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-2P5-4-B2
R3020-2P5-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 2.5 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-2P5-P63-B2
R3020-4-1-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 4 m³/h Kvs (Sequence 2) 1 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-4-1-B2
R3020-4-1P6-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 4 m³/h Kvs (Sequence 2) 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-4-1P6-B2
R3020-4-2P5-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 4 m³/h Kvs (Sequence 2) 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-4-2P5-B2
R3020-4-4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 4 m³/h Kvs (Sequence 2) 4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-4-4-B2
R3020-4-P63-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 4 m³/h Kvs (Sequence 2) 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-4-P63-B2
R3020-4-S2 | 3-way Characterised control valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3020-4-S2
R3020-6P3-S2 | 3-way Characterised control valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3020-6P3-S2
R3020-BL2 | 3-way Changeover ball valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 11 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-BL2
R3020-P63-1P6-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-P63-1P6-B2
R3020-P63-2P5-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-P63-2P5-B2
R3020-P63-4-B2 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 20, PN 16 Internal thread Rp 3/4" Kvs (Sequence 1) 0.63 m³/h Kvs (Sequence 2) 4 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3020-P63-4-B2
R3020-S2 | 3-way Changeover ball valve DN 20, PN 40 Internal thread Rp 3/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3020-S2
R3025-10-S2 | 3-way Characterised control valve DN 25, PN 40 Internal thread Rp 1" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3025-10-S2
R3025-6P3-6P3-B3 | 6-way Characterised control valve Integrated self-cleaning pressure relief function Constructive dead zone for safe locking when switching from heating to cooling DN 25, PN 16 Internal thread Rp 1" Kvs (Sequence 1) 6.3 m³/h Kvs (Sequence 2) 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature 6...80°C [43...176°F] Characteristic curve linear Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3025-6P3-6P3-B3
R3025-6P3-S2 | 3-way Characterised control valve DN 25, PN 40 Internal thread Rp 1" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3025-6P3-S2
R3025-BL2 | 3-way Changeover ball valve DN 25, PN 40 Internal thread Rp 1" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3025-BL2
R3025-S2 | 3-way Changeover ball valve DN 25, PN 40 Internal thread Rp 1" Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3025-S2
R3032-16-S3 | 3-way Characterised control valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3032-16-S3
R3032-BL2 | 3-way Changeover ball valve DN 32, PN 40 Internal thread Rp 1 1/4" Kvs 9 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3032-BL2
R3032-BL3 | 3-way Changeover ball valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 15 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3032-BL3
R3032-S3 | 3-way Changeover ball valve DN 32, PN 25 Internal thread Rp 1 1/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3032-S3
R3040-16-S3 | 3-way Characterised control valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3040-16-S3
R3040-25-S4 | 3-way Characterised control valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3040-25-S4
R3040-BL3 | 3-way Changeover ball valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 14 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3040-BL3
R3040-BL4 | 3-way Changeover ball valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 47 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3040-BL4
R3040-S3 | 3-way Changeover ball valve DN 40, PN 25 Internal thread Rp 1 1/2" Kvs 31 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3040-S3
R3050-25-S4 | 3-way Characterised control valve DN 50, PN 25 Internal thread Rp 2" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3050-25-S4
R3050-40-S4 | 3-way Characterised control valve DN 50, PN 25 Internal thread Rp 2" Kvs 40 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3050-40-S4
R3050-58-S4 | 3-way Characterised control valve DN 50, PN 25 Internal thread Rp 2" Kvs 58 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R3050-58-S4
R3050-BL3 | 3-way Changeover ball valve DN 50, PN 25 Internal thread Rp 2" Kvs 24 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3050-BL3
R3050-BL4 | 3-way Changeover ball valve DN 50, PN 25 Internal thread Rp 2" Kvs 75 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R3050-BL4
R3050-S4 | 3-way Changeover ball valve DN 50, PN 25 Internal thread Rp 2" Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...120°C [14...248°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R3050-S4
R404DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 0.3 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R404DK
R405DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 0.4 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R405DK
R406DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 0.63 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R406DK
R407DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 1 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R407DK
R408DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 1.6 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R408DK
R409 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R409
R409DK | 2-way Characterised control valve DN 10, PN 40 External thread G 3/4" Kvs 2.5 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R409DK
R410 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 1 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R410
R410DK | 2-way Open/close ball valve DN 10, PN 40 External thread G 3/4" Kvs 4 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R410DK
R411 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R411
R412 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R412
R412D | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 2.5 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R412D
R413 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R413
R413D | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 4 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R413D
R414 | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R414
R414D | 2-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 6.3 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R414D
R415 | 2-way Open/close ball valve DN 15, PN 40 External thread G 1" Kvs 8.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R415
R415D | 2-way Open/close ball valve DN 15, PN 40 External thread G 1" Kvs 12 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R415D
R417 | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R417
R417D | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 6.3 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R417D
R418 | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R418
R418D | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 10 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R418D
R419 | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 8.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R419
R419D | 2-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 16 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R419D
R420 | 2-way Open/close ball valve DN 20, PN 40 External thread G 1 1/4" Kvs 21 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R420
R420D | 2-way Open/close ball valve DN 20, PN 40 External thread G 1 1/4" Kvs 25 m³/h Valve body Low lead red brass (CuSn4Zn6Pb3) Fluid temperature 2...130°C [36...266°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R420D
R422 | 2-way Characterised control valve DN 25, PN 40 External thread G 1 1/2" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R422
R423 | 2-way Characterised control valve DN 25, PN 40 External thread G 1 1/2" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R423
R424 | 2-way Characterised control valve DN 25, PN 40 External thread G 1 1/2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R424
R425 | 2-way Open/close ball valve DN 25, PN 40 External thread G 1 1/2" Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R425
R431 | 2-way Characterised control valve DN 32, PN 25 External thread G 2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R431
R432 | 2-way Open/close ball valve DN 32, PN 25 External thread G 2" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R432
R438 | 2-way Characterised control valve DN 40, PN 25 External thread G 2 1/4" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R438
R439 | 2-way Characterised control valve DN 40, PN 25 External thread G 2 1/4" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R439
R440 | 2-way Open/close ball valve DN 40, PN 25 External thread G 2 1/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R440
R448 | 2-way Characterised control valve DN 50, PN 25 External thread G 2 3/4" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R448
R449 | 2-way Characterised control valve DN 50, PN 25 External thread G 2 3/4" Kvs 40 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R449
R450 | 2-way Open/close ball valve DN 50, PN 25 External thread G 2 3/4" Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R450
R509 | 3-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R509
R510 | 3-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 1 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R510
R511 | 3-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R511
R512 | 3-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R512
R513 | 3-way Characterised control valve DN 15, PN 40 External thread G 1" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R513
R515 | 3-way Changeover ball valve DN 15, PN 40 External thread G 1" Kvs 8.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R515
R517 | 3-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R517
R518 | 3-way Characterised control valve DN 20, PN 40 External thread G 1 1/4" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R518
R520 | 3-way Changeover ball valve DN 20, PN 40 External thread G 1 1/4" Kvs 21 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R520
R522 | 3-way Characterised control valve DN 25, PN 40 External thread G 1 1/2" Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R522
R523 | 3-way Characterised control valve DN 25, PN 40 External thread G 1 1/2" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R523
R525 | 3-way Changeover ball valve DN 25, PN 40 External thread G 1 1/2" Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R525
R529 | 3-way Characterised control valve DN 32, PN 40 External thread G 2" Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R529
R530 | 3-way Changeover ball valve DN 32, PN 40 External thread G 2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R530
R531 | 3-way Characterised control valve DN 32, PN 25 External thread G 2" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R531
R532 | 3-way Changeover ball valve DN 32, PN 25 External thread G 2" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R532
R538 | 3-way Characterised control valve DN 40, PN 25 External thread G 2 1/4" Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R538
R540 | 3-way Changeover ball valve DN 40, PN 25 External thread G 2 1/4" Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R540
R548 | 3-way Characterised control valve DN 50, PN 25 External thread G 2 3/4" Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R548
R550 | 3-way Changeover ball valve DN 50, PN 25 External thread G 2 3/4" Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R550
R6015R-B1 | 2-way Open/close ball valve DN 15, PN 6 Flange Kvs 15 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015R-B1
R6015R1-B1 | 2-way Characterised control valve DN 15, PN 6 Flange Kvs 1 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015R1-B1
R6015R1P6-B1 | 2-way Characterised control valve DN 15, PN 6 Flange Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015R1P6-B1
R6015R2P5-B1 | 2-way Characterised control valve DN 15, PN 6 Flange Kvs 2.5 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015R2P5-B1
R6015R4-B1 | 2-way Characterised control valve DN 15, PN 6 Flange Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015R4-B1
R6015RP63-B1 | 2-way Characterised control valve DN 15, PN 6 Flange Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6015RP63-B1
R6020R-B1 | 2-way Open/close ball valve DN 20, PN 6 Flange Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6020R-B1
R6020R6P3-B1 | 2-way Characterised control valve DN 20, PN 6 Flange Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6020R6P3-B1
R6025R-B2 | 2-way Open/close ball valve DN 25, PN 6 Flange Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6025R-B2
R6025R10-B2 | 2-way Characterised control valve DN 25, PN 6 Flange Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6025R10-B2
R6032R-B3 | 2-way Open/close ball valve DN 32, PN 6 Flange Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6032R-B3
R6032R16-B3 | 2-way Characterised control valve DN 32, PN 6 Flange Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6032R16-B3
R6040R-B3 | 2-way Open/close ball valve DN 40, PN 6 Flange Kvs 31 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6040R-B3
R6040R25-B3 | 2-way Characterised control valve DN 40, PN 6 Flange Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6040R25-B3
R6050R-B3 | 2-way Open/close ball valve DN 50, PN 6 Flange Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6050R-B3
R6050R40-B3 | 2-way Characterised control valve DN 50, PN 6 Flange Kvs 40 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6050R40-B3
R6065W63-S8 | 2-way Characterised control valve DN 65, PN 16 Flange Kvs 63 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6065W63-S8
R6080W100-S8 | 2-way Characterised control valve DN 80, PN 16 Flange Kvs 100 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6080W100-S8
R6100W160-S8 | 2-way Characterised control valve DN 100, PN 16 Flange Kvs 160 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6100W160-S8
R6125W250-S8 | 2-way Characterised control valve DN 125, PN 16 Flange Kvs 250 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6125W250-S8
R6150W320-S8 | 2-way Characterised control valve DN 150, PN 16 Flange Kvs 320 m³/h Valve body EN-GJL-250 (GG 25) Fluid temperature -10...120°C [14...248°F] Characteristic curve equal percentage Leakage rate air-bubble tight, leakage rate A Manufacturer Belimo Type R6150W320-S8
R7015R-B1 | 3-way Changeover ball valve DN 15, PN 6 Flange Kvs 15 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7015R-B1
R7015R1P6-B1 | 3-way Characterised control valve DN 15, PN 6 Flange Kvs 1.6 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7015R1P6-B1
R7015R4-B1 | 3-way Characterised control valve DN 15, PN 6 Flange Kvs 4 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7015R4-B1
R7015RP63-B1 | 3-way Characterised control valve DN 15, PN 6 Flange Kvs 0.63 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7015RP63-B1
R7020R-B1 | 3-way Changeover ball valve DN 20, PN 6 Flange Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7020R-B1
R7020R6P3-B1 | 3-way Characterised control valve DN 20, PN 6 Flange Kvs 6.3 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7020R6P3-B1
R7025R-B2 | 3-way Changeover ball valve DN 25, PN 6 Flange Kvs 26 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7025R-B2
R7025R10-B2 | 3-way Characterised control valve DN 25, PN 6 Flange Kvs 10 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7025R10-B2
R7032R-B3 | 3-way Changeover ball valve DN 32, PN 6 Flange Kvs 32 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7032R-B3
R7032R16-B3 | 3-way Characterised control valve DN 32, PN 6 Flange Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7032R16-B3
R7040R-B3 | 3-way Changeover ball valve DN 40, PN 6 Flange Kvs 31 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7040R-B3
R7040R16-B3 | 3-way Characterised control valve DN 40, PN 6 Flange Kvs 16 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7040R16-B3
R7050R-B3 | 3-way Changeover ball valve DN 50, PN 6 Flange Kvs 49 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, max. 1% of the Kvs value Manufacturer Belimo Type R7050R-B3
R7050R25-B3 | 3-way Characterised control valve DN 50, PN 6 Flange Kvs 25 m³/h Valve body Nickel-plated brass body Fluid temperature -10...100°C [14...212°F] Characteristic curve A – AB: equal percentage; B – AB: linear Leakage rate A – AB: air-bubble tight, leakage rate A; B – AB: Leakage class I, 1...2% of the Kvs value Manufacturer Belimo Type R7050R25-B3
RV24A-MF | Parametrisable electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 4500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.5 W Power consumption for wire sizing 11 VA Control modulating ConfigurableShort MFT Running time motor 150 s / 50 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type RV24A-MF
RV24A-MF-RE | Parametrisable electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 4500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.5 W Power consumption for wire sizing 11 VA Control modulating ConfigurableShort MFT Running time motor 150 s / 50 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type RV24A-MF-RE
RV24A-SR | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 4500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.5 W Power consumption for wire sizing 11 VA Control modulating Running time motor 150 s / 50 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type RV24A-SR
RV24A-SZ | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 4500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.5 W Power consumption for wire sizing 11 VA Control modulating Running time motor 150 s / 50 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type RV24A-SZ
S1A | Auxiliary switch add-on 1x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 1 m PVC
S2A | Auxiliary switch add-on 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 1 m PVC
S2A GR | Auxiliary switch add-on, grey 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 1 m FRNC
S2A-F | Auxiliary switch 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % incl. installation accessories Cable 1 m PVC
S2A-H | Auxiliary switch add-on 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 1 m PVC
S2A/300 GR | Auxiliary switch add-on, grey 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 3 m FRNC
S2A/500 GR | Auxiliary switch add-on, grey 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 5 m FRNC
SB-TF | Screw fastening kit for short damper shafts minimum length 20 mm for flat and side installation Galvanised steel Thermo-plastic material
SBG24 | Range controller for wall mounting Electronically adjustable min./max. angle of rotation limiting only ...-SR, ...-MF, ..-MP Terminals 4 mm²
SF24A | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A
SF24A-3 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7.5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 10 VA Control 3-point Running time motor 150 s / 90° Running time fail-safe <20 s Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-3
SF24A-MF | Parametrisable fail-safe damper actuator Torque motor 20 Nm Running time motor 150 s Torque fail-safe 20 Nm Running time fail-safe <20 s Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating Electrical connection Cable 1 m, with plug Universal shaft clamp 10...25.4 mm Manual override by means of hand crank and locking switch Direction of motion selectable with switch L/R Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-MF
SF24A-MOD | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-MOD
SF24A-MP | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-MP
SF24A-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-S2
SF24A-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-SR
SF24A-SR-S2 | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-SR-S2
SF24A-SZ | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-SZ
SF24A-SZ-S2 | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-SZ-S2
SF24A-VST | VAV-Universal fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control communicative PP Running time motor 120 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24A-VST
SF24G-MP-L | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 9.5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24G-MP-L
SF24G-SR-L | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24G-SR-L
SF24G-SR-S2-L | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 3 W Power consumption for wire sizing 7 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SF24G-SR-S2-L
SFA | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SFA
SFA-S2 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SFA-S2
SFG-L | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SFG-L
SFG-S2-L | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Angle of rotation Max. 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SFG-S2-L
SGA24 | Positioner for wall mounting 0...100% operating range selectable 0...10 V or 2...10 V Terminals 1.5 mm²
SGE24 | Positioner for built-in mounting 0...100% operating range selectable 0...10 V or 2...10 V Terminals 4 mm²
SGF24 | Positioner for front-panel mounting 0...100% operating range selectable 0...10 V or 2...10 V Terminals 1.5 mm²
SH230A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SH230A100
SH230A200 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SH230A200
SH230A300 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SH230A300
SH230ASR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SH230ASR100
SH230ASR200 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 1 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 200 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SH230ASR200
SH24A-MOD200 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-MOD200
SH24A-MP100 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-MP100
SH24A-MP200 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-MP200
SH24A-MP300 | Communicative linear actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-MP300
SH24A-SR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4.5 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-SR100
SH24A-SR200 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4.5 VA Control modulating Running time motor 150 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 200 mm, fixed setting Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A-SR200
SH24A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A100
SH24A200 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 200 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A200
SH24A300 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 450 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 150 s / 100 mm Length of Stroke Max. 300 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SH24A300
SHQ24A-MF100 | Parametrisable linear actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 200 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating ConfigurableShort MFT Running time motor 7 s / 100 mm Operating range 2...10 V variable Position feedback 2...10 V variable Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SHQ24A-MF100
SHQ24A-SR100 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 200 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control modulating Running time motor 7 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SHQ24A-SR100
SHQ24A100 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 200 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 2 W Power consumption for wire sizing 23 VA Control Open/close Running time motor 7 s / 100 mm Length of Stroke Max. 100 mm, adjustable in 20 mm increments Direction of motion motor selectable with switch 0 (extended) / 1 (retracted) Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SHQ24A100
SKM230-T-B12.1 | Power module for CM..K.. damper actuator Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 16 W Power consumption in rest position 1.5 W Power consumption for wire sizing 24 VA Control Open/close Electrical connection Terminals Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Multipack 10 pcs. Manufacturer Belimo Type SKM230-T-B12.1
SM230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230A
SM230A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230A-S
SM230A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230A-S-TP
SM230A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230A-TP
SM230ASR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230ASR
SM230ASR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230ASR-TP
SM230P | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230P
SM230P-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.6 W Power consumption for wire sizing 6 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230P-S
SM230PSR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SM230PSR
SM24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A
SM24A-MA | Parametrisable damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating Running time motor 150 s / 90° Operating range 4...20 mA Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-MA
SM24A-MOD | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-MOD
SM24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-MP
SM24A-MP-TP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-MP-TP
SM24A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-S
SM24A-S-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-S-TP
SM24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-SR
SM24A-SR-TP | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-SR-TP
SM24A-TP | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-TP
SM24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control communicative PP Running time motor 120 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24A-VST
SM24AP5 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 90° Feedback potentiometer 5 kΩ Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24AP5
SM24P | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24P
SM24P-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24P-MP
SM24P-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.2 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 150 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24P-S
SM24P-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.4 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 14...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SM24P-SR
SMC24A-MOD | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 35 s / 90° Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMC24A-MOD
SMC24A-MP | Communicative damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 7 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMC24A-MP
SMD230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1 W Power consumption for wire sizing 8 VA Control Open/close, 3-point Running time motor 20 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SMD230A
SMD24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 0.5 W Power consumption for wire sizing 6.5 VA Control Open/close, 3-point Running time motor 20 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMD24A
SMQ24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control Open/close Running time motor 7 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24A
SMQ24A-MF | Parametrisable damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control modulating ConfigurableShort MFT Running time motor 7 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24A-MF
SMQ24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control modulating Running time motor 7 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24A-SR
SMQ24A-VST | VAV-Universal damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control communicative PP Running time motor 7 s / 90° Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 0.5 m PVC with VST connector Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24A-VST
SMQ24G | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control Open/close Running time motor 7 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24G
SMQ24G-MF | Parametrisable damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control modulating ConfigurableShort MFT Running time motor 7 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24G-MF
SMQ24G-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control modulating Running time motor 7 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked (under protective housing) Mechanical interface Universal shaft clamp 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SMQ24G-SR
SMV-D3-MOD | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6.5 VA Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type SMV-D3-MOD
SMV-D3-MP | VAV-Compact device – with VAV controller, dynamic Δp sensor and damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Control communicative, modulating Communication MP-Bus Operating range 2...10 V Feedback volume/position/diff. pressure 2...10 V Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 10...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Protective Extra-Low Voltage (PELV) Manufacturer Belimo Type SMV-D3-MP
SN2-C7 | Auxiliary switch 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 1 m FRNC
SN2-C7/300 | Auxiliary switch cable length 3 m 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 3 m FRNC
SN2-C7/500 | Auxiliary switch cable length 5 m 2x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable 5 m FRNC
SNR | Auxiliary switch for 3-point HT actuators with cable connection 1x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable gland for 1 cable not for modulating or open/close actuators Terminals
SNR2 | Auxiliary switch for 3-point HT actuators with screw terminals 1x SPDT 1mA...3 (0.5) A, AC 250 V Adjustable switching point 0...100 % Cable gland for 2 cable not for modulating or open/close actuators Terminals
SR230A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230A
SR230A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230A-5
SR230A-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230A-R
SR230A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230A-S
SR230A-SR-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1 W Power consumption for wire sizing 7.5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230A-SR-5
SR230P | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230P
SR230P-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230P-5
SR230P-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3 W Power consumption in rest position 0.6 W Power consumption for wire sizing 7 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SR230P-R
SR24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A
SR24A-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-5
SR24A-MOD | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MOD
SR24A-MOD-5 | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.25 W Power consumption for wire sizing 7 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MOD-5
SR24A-MOD-J6 | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control communicative Communication BACnet MS/TP, Modbus RTU Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Connector socket RJ12 Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MOD-J6
SR24A-MP | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MP
SR24A-MP-5 | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MP-5
SR24A-MP-R | Communicative electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-MP-R
SR24A-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-R
SR24A-S | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-S
SR24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-SR
SR24A-SR-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-SR-5
SR24A-SR-TP | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-SR-TP
SR24A-SZ | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-SZ
SR24A-SZ-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24A-SZ-5
SR24P | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P
SR24P-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P-5
SR24P-MP-R | Electronic rotary actuator for ball valves and butterfly valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.25 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P-MP-R
SR24P-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 5.5 VA Control Open/close, 3-point Running time motor 90 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P-R
SR24P-SR | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P-SR
SR24P-SR-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 5 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP66/67 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SR24P-SR-5
SRC24A-MP | Communicative electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRC24A-MP
SRC24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRC24A-SR
SRC24A-SR-5 | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRC24A-SR-5
SRD230A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1 W Power consumption for wire sizing 8 VA Control Open/close, 3-point Running time motor 20 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRD230A
SRF24A | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A
SRF24A-5 | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-5
SRF24A-5-O | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-5-O
SRF24A-MOD | Communicative electronic fail-safe rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Deenergised closed (NC) Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-MOD
SRF24A-MOD-O | Communicative electronic fail-safe rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Deenergised open (NO) Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 90 s / 90° Running time fail-safe <20 s Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-MOD-O
SRF24A-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-O
SRF24A-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-R
SRF24A-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-S2
SRF24A-S2-5 | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-S2-5
SRF24A-S2-5-O | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-S2-5-O
SRF24A-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-S2-O
SRF24A-S2-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5 W Power consumption in rest position 2.5 W Power consumption for wire sizing 7.5 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-S2-R
SRF24A-SR | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR
SRF24A-SR-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-5
SRF24A-SR-5-O | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-5-O
SRF24A-SR-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-O
SRF24A-SR-S2 | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-S2
SRF24A-SR-S2-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-S2-5
SRF24A-SR-S2-5-O | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-S2-5-O
SRF24A-SR-S2-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SR-S2-O
SRF24A-SZ | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ
SRF24A-SZ-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-5
SRF24A-SZ-5-O | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-5-O
SRF24A-SZ-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-O
SRF24A-SZ-S2 | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-S2
SRF24A-SZ-S2-5 | Modulating electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-S2-5
SRF24A-SZ-S2-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 3 W Power consumption for wire sizing 8.5 VA Control modulating Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 0.5...10 V Position feedback 0.5...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRF24A-SZ-S2-O
SRFA | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA
SRFA-5 | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-5
SRFA-5-O | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-5-O
SRFA-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-O
SRFA-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3 W Power consumption for wire sizing 18 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-R
SRFA-S2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-S2
SRFA-S2-5 | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-S2-5
SRFA-S2-5-O | Electronic fail-safe rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-S2-5-O
SRFA-S2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-S2-O
SRFA-S2-R | Electronic rotary actuator for ball valves and butterfly valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC 24...240 V / DC 24...125 V Nominal voltage frequency 50/60 Hz Power consumption in operation 7 W Power consumption in rest position 3.5 W Power consumption for wire sizing 18 VA Control Open/close Auxiliary switch 2x SPDT Auxiliary switch note 1x 10% / 1x 11...100% Running time motor 75 s / 90° Running time fail-safe <20 s Manual override by means of hand crank and locking switch Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SRFA-S2-R
SRQ24A | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 16 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 15 W Power consumption in rest position 2 W Power consumption for wire sizing 26 VA Control Open/close Running time motor 9 s / 90° Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SRQ24A
SV230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SV230A-RE
SV230A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SV230A-TPC
SV24A-MOD | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 3.5 VA Control modulating, communicative, hybrid Communication BACnet MS/TP, Modbus RTU, MP-Bus Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-MOD
SV24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-MP-RE
SV24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 3.5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-MP-TPC
SV24A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-RE
SV24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 3.5 VA Control modulating Running time motor 150 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-SR-TPC
SV24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 3.5 VA Control modulating Running time motor 150 s / 20 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-SZ-TPC
SV24A-TPC | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 5 VA Control Open/close, 3-point Running time motor 150 s / 20 mm Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SV24A-TPC
SVC24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SVC24A-MP-RE
SVC24A-MP-TPC | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating, communicative Communication MP-Bus Running time motor 35 s / 20 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SVC24A-MP-TPC
SVC24A-SR-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 35 s / 20 mm Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SVC24A-SR-TPC
SVC24A-SZ-TPC | Modulating electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4 W Power consumption in rest position 1.5 W Power consumption for wire sizing 6 VA Control modulating Running time motor 35 s / 20 mm Operating range 0.5...10 V Position feedback 0.5...10 V Manual override with push-button, can be locked Electrical connection Terminals with cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SVC24A-SZ-TPC
SVL230A-RE | Electronic globe valve actuator for globe valves Current reduction in rest position Constant, load-independent running time Actuating force motor 1500 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1 W Power consumption for wire sizing 6.5 VA Control Open/close, 3-point Running time motor 150 s / 50 mm Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type SVL230A-RE
SVL24A-MP-RE | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Actuating force motor 1500 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 50 mm Operating range 2...10 V variable Position feedback 2...10 V variable Manual override with push-button, can be locked Electrical connection Terminals Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type SVL24A-MP-RE
SY10-230A-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 2500 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 398 W Power consumption for wire sizing 437 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 76 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY10-230A-3-T
SY12-230A-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 3500 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 424 W Power consumption for wire sizing 460 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 76 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY12-230A-3-T
SY4-230-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 400 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 297 W Power consumption for wire sizing 299 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 23 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY4-230-3-T
SY4-24-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 400 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 195 W Power consumption for wire sizing 226 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 20 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY4-24-3-T
SY5-230-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 500 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 297 W Power consumption for wire sizing 299 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 30 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY5-230-3-T
SY6-230-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 650 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 297 W Power consumption for wire sizing 299 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 40 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY6-230-3-T
SY7-230A-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 1000 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 699 W Power consumption for wire sizing 759 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 60 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY7-230A-3-T
SY8-230A-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 1500 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 722 W Power consumption for wire sizing 759 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 60 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY8-230A-3-T
SY9-230A-3-T | Electronic rotary actuator for butterfly valves Constant, load-independent running time Torque motor 2000 Nm Nominal voltage AC 230 V Nominal voltage frequency 50/60 Hz Power consumption in operation 381 W Power consumption for wire sizing 414 VA Control Open/close, 3-point Auxiliary switch 2x SPDT Auxiliary switch note 1x 3° / 1x 87° Running time motor 76 s / 90° Angle of rotation 90° Manual override temporary with handwheel (non-rotating) Electrical connection Terminals Degree of protection IEC/EN IP67 Protection class IEC/EN I, protective earth (PE) Manufacturer Belimo Type SY9-230A-3-T
TF230 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TF230
TF230-S | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TF230-S
TF230-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 2 W Power consumption for wire sizing 5 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <25 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TF230-SR
TF24 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TF24
TF24-3 | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control 3-point Running time motor 150 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TF24-3
TF24-MFT | Communicative fail-safe damper actuator Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating, communicative Communication MP-Bus Running time motor 150 s / 90° Running time fail-safe <25 s / 90° Operating range 2...10 V variable Position feedback 2...10 V variable Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TF24-MFT
TF24-S | Fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor selectable by mounting L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TF24-S
TF24-SR | Modulating fail-safe damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating Running time motor 150 s / 90° Running time fail-safe <25 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch L/R Angle of rotation Max. 95° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TF24-SR
TMC230A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TMC230A
TMC230A-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TMC230A-F
TMC230A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TMC230A-S
TMC230A-S-F | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 0.5 W Power consumption for wire sizing 4 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TMC230A-S-F
TMC230ASR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1 W Power consumption for wire sizing 3.5 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TMC230ASR
TMC24A | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TMC24A
TMC24A-S | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.2 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 35 s / 90° Direction of motion motor selectable with switch 0 (ccw rotation) / 1 (cw rotation) Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TMC24A-S
TMC24A-SR | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TMC24A-SR
TMC24A-SR-F | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor selectable with switch 0/1 Angle of rotation Max. 95° Manual override with push-button, can be locked Mechanical interface Form fit 8x8 mm Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TMC24A-SR-F
TR230-3 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 230 V Nominal voltage frequency 50 Hz Power consumption in operation 1 W Power consumption for wire sizing 1 VA Control 3-point Running time motor 105 s / 90° Manual override with hand crank Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TR230-3
TR24 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption for wire sizing 0.5 VA Control Open/close, 3-point Running time motor 100 s / 90° Manual override temporary gear train disengagement Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TR24
TR24-SR | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption for wire sizing 1 VA Control modulating Running time motor 90 s / 90° Operating range 2...10 V Manual override temporary gear train disengagement Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TR24-SR
TRC24A-SR | Modulating electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.4 W Power consumption for wire sizing 3 VA Control modulating Running time motor 15 s / 90° Operating range 2...10 V Position feedback 2...10 V Manual override with push-button, can be locked Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP54 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRC24A-SR
TRF230 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TRF230
TRF230-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TRF230-O
TRF230-S | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TRF230-S
TRF230-S-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TRF230-S-O
TRF24 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24
TRF24-2 | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control 3-point Running time motor 90 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor Y = 0 (A – AB = 0%) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-2
TRF24-2-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control 3-point Running time motor 90 s / 90° Running time fail-safe <25 s / 90° Direction of motion motor Y = 0 (A – AB = 0%) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-2-O
TRF24-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-O
TRF24-S | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-S
TRF24-S-O | Electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 5 VA Control Open/close Auxiliary switch 1x SPDT Auxiliary switch note 0...100% Running time motor 75 s / 90° Running time fail-safe <75 s / 90° Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-S-O
TRF24-SR | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised closed (NC) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <25 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-SR
TRF24-SR-O | Modulating electronic fail-safe rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Deenergised open (NO) Torque motor 2.5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2.5 W Power consumption in rest position 1 W Power consumption for wire sizing 4 VA Control modulating Running time motor 90 s / 90° Running time fail-safe <25 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor Y = 0 (0 V = A – AB = 0%) Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRF24-SR-O
TRY230 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2.5 VA Control Open/close, 3-point Running time motor 35 s / 90° Manual override with hand crank Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN II, reinforced insulation Manufacturer Belimo Type TRY230
TRY24 | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption for wire sizing 0.5 VA Control Open/close, 3-point Running time motor 35 s / 90° Manual override with hand crank Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRY24
TRY24-SR | Electronic rotary actuator for ball valves Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 2 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 0.5 W Power consumption for wire sizing 1 VA Control modulating Running time motor 35 s / 90° Operating range 2...10 V Manual override with hand crank Electrical connection Cable 1 m PVC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type TRY24-SR
UH230Y-L.1 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 50 N Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 122 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 1 mm increments Direction of motion motor by electrical installation Manual override No Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 40 pcs. Manufacturer Belimo Type UH230Y-L.1
UH24Y-L.1 | Linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 50 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 122 s / 100 mm Length of Stroke Max. 60 mm, adjustable in 1 mm increments Direction of motion motor by electrical installation Manual override No Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 40 pcs. Manufacturer Belimo Type UH24Y-L.1
UH24Y-SR-L.1 | Modulating linear actuator Current reduction in rest position Constant, load-independent running time Actuating force motor 50 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 122 s / 100 mm Operating range 2...10 V Position feedback 2...10 V Length of Stroke Max. 60 mm, adjustable in 1 mm increments Direction of motion motor counter-clockwise rotation Manual override No Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 40 pcs. Manufacturer Belimo Type UH24Y-SR-L.1
UK24BAC | Gateway MP to BACnet MS/TP AC/DC 24 V Converting MP-Bus to BACnet MS/TP (RS-485) Connection of maximum of 8 actuators MP/MPL/MFT(2) incl. VAV and fire protection
UK24MOD | Gateway MP to Modbus RTU AC/DC 24 V Converting MP-Bus to Modbus RTU (RS-485) Connection of maximum of 8 actuators MP/MPL/MFT(2) incl. VAV and fire protection
UM230Y-F-L.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 100 pcs. Manufacturer Belimo Type UM230Y-F-L.1
UM230Y-F-R.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 100 pcs. Manufacturer Belimo Type UM230Y-F-R.1
UM230Y-F10-L.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override No Mechanical interface Form fit 10x10 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 100 pcs. Manufacturer Belimo Type UM230Y-F10-L.1
UM230Y-L.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...185° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 100 pcs. Manufacturer Belimo Type UM230Y-L.1
UM230Y-R.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC 100...240 V Nominal voltage frequency 50/60 Hz Power consumption in operation 2 W Power consumption in rest position 1.5 W Power consumption for wire sizing 4.5 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...185° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN 0, basic insulation Multipack 100 pcs. Manufacturer Belimo Type UM230Y-R.1
UM24Y-F-L.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...287.5° Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-F-L.1
UM24Y-F-R.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...287.5° Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-F-R.1
UM24Y-L.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor counter-clockwise rotation Angle of rotation 0...185° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-L.1
UM24Y-R.1 | Damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2 VA Control Open/close, 3-point Running time motor 22 s / 90° Direction of motion motor clockwise rotation Angle of rotation 0...185° Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-R.1
UM24Y-SR-F-L.1 | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 22 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-SR-F-L.1
UM24Y-SR-F-R.1 | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 22 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override No Mechanical interface Form fit 8x8 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-SR-F-R.1
UM24Y-SR-L.1 | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 22 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor counter-clockwise rotation Angle of rotation 95°, fixed setting Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-SR-L.1
UM24Y-SR-R.1 | Modulating damper actuator Current reduction in rest position Constant, load-independent running time Mechanical angle of rotation limiter and position indication Torque motor 1 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 2.5 VA Control modulating Running time motor 22 s / 90° Operating range 2...10 V Position feedback 2...10 V Direction of motion motor clockwise rotation Angle of rotation 95°, fixed setting Manual override No Mechanical interface Universal shaft clamp 6...12.7 mm Electrical connection Connector plug Degree of protection IEC/EN IP20 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Multipack 100 pcs. Manufacturer Belimo Type UM24Y-SR-R.1
VGM24A-LP1 | Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 1.6 W Power consumption for wire sizing 8 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback variable Direction of motion motor selectable with switch 0/1 Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 12...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VGM24A-LP1
VGR24A-LP1-5 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 5.5 W Power consumption in rest position 1.5 W Power consumption for wire sizing 8 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VGR24A-LP1-5
VGRK24A-LP1-5 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 40 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 11 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VGRK24A-LP1-5
VLM24A-LP1 | Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 3 W Power consumption for wire sizing 5 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback variable Direction of motion motor selectable with switch 0/1 Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 6...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VLM24A-LP1
VLR24A-LP1 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 5 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 3.5 W Power consumption in rest position 3 W Power consumption for wire sizing 5 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VLR24A-LP1
VNM24A-LP1 | Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.4 W Power consumption for wire sizing 6.5 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback variable Direction of motion motor selectable with switch 0/1 Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp 8...26.7 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VNM24A-LP1
VNR24A-LP1 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 10 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 4.5 W Power consumption in rest position 1.2 W Power consumption for wire sizing 6.5 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VNR24A-LP1
VNV24A-LP1 | Communicative electronic globe valve actuator for globe valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Actuating force motor 1000 N Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption in rest position 0.5 W Power consumption for wire sizing 3 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 20 mm Operating range 2...10 V variable Position feedback variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VNV24A-LP1
VRU-D3-BAC | VAV-Universal – modular VAV/duct pressure control solution with dynamic Δp sensor Conversion of sensor signals NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2 VA plus connected VST actuator Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Electrical connection Terminals suitable for ...-VST actuator Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VRU-D3-BAC
VRU-M1-BAC | VAV-Universal – modular control solution with integrated Δp sensor for contaminated media Conversion of sensor signals NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2 VA plus connected VST actuator Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Electrical connection Terminals suitable for ...-VST actuator Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VRU-M1-BAC
VRU-M1-BAC-RE | VAV-Universal – modular control solution with integrated Δp sensor for contaminated media Conversion of sensor signals NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2 VA plus connected VST actuator Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Electrical connection Terminals suitable for ...-VST-RE actuator Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VRU-M1-BAC-RE
VRU-M1R-BAC | VAV-Universal – modular control solution with integrated Δp sensor for contaminated media Conversion of sensor signals NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2 VA plus connected VST actuator Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Electrical connection Terminals suitable for ...-VST actuator Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VRU-M1R-BAC
VRU-M1R-BAC-RE | VAV-Universal – modular control solution with integrated Δp sensor for contaminated media Conversion of sensor signals NFC interface without external energy NFC interface for commissioning, parametrisation and maintenance with Belimo Assistant App Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 1.5 W Power consumption for wire sizing 2 VA plus connected VST actuator Control communicative, hybrid, modulating Communication BACnet MS/TP, Modbus RTU, MP-Bus Operating range 2...10 V Electrical connection Terminals suitable for ...-VST-RE actuator Degree of protection IEC/EN IP42 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VRU-M1R-BAC-RE
VSF24A-LP1 | Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 8.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 11 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback variable Direction of motion motor selectable with switch L/R Angle of rotation 95° Manual override by means of hand crank and locking switch Mechanical interface Universal shaft clamp 10...25.4 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VSF24A-LP1
VSM24A-LP1 | Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.4 W Power consumption for wire sizing 8 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 150 s / 90° Operating range 2...10 V variable Position feedback variable Direction of motion motor selectable with switch 0/1 Angle of rotation 95° Manual override with push-button, can be locked Mechanical interface Universal shaft clamp reversible 10...20 mm Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VSM24A-LP1
VSR24A-LP1 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 6 W Power consumption in rest position 1.25 W Power consumption for wire sizing 8 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button, can be locked Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VSR24A-LP1
VSRF24A-LP1 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 9.5 W Power consumption in rest position 3.5 W Power consumption for wire sizing 14 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Running time fail-safe <20 s Operating range 2...10 V variable Position feedback variable Direction of motion motor Y = 0 (0 V = A – AB = 0%) Manual override by means of hand crank and locking switch Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VSRF24A-LP1
VSRK24A-LP1 | Cloud capable electronic rotary actuator for ball valves Conversion of sensor signals Current reduction in rest position Constant, load-independent running time Adaptable setting range Mechanical angle of rotation limiter and position indication Torque motor 20 Nm Nominal voltage AC/DC 24 V Nominal voltage frequency 50/60 Hz Power consumption in operation 13 W Power consumption in rest position 3 W Power consumption for wire sizing 21 VA Control modulating, communicative, hybrid, Cloud Communication Cloud, BACnet/IP, Modbus TCP Running time motor 90 s / 90° Running time fail-safe 35 s / 90° Operating range 2...10 V variable Position feedback variable Manual override with push-button Electrical connection Cable 1 m FRNC Degree of protection IEC/EN IP40 Protection class IEC/EN III, Safety Extra-Low Voltage (SELV) Manufacturer Belimo Type VSRK24A-LP1
Z-ARCM | Anti-rotation clip for CM.. / UM.. Thermo-plastic material Multipack 20 pcs.
Z-ARCM.1
Z-ARS180 | Anti-rotation mechanism 180 mm for TM...A, LM..A, NM..A, TF anti-rotation brackets 179x18 mm, bolts short incl. 2 screws Multipack 20 pcs.
Z-ARS180L | Anti-rotation mechanism 180 mm for LF.. anti-rotation brackets 179x18 mm, bolts long incl. 2 screws Multipack 20 pcs.
Z-ARS230 | Anti-rotation mechanism 230 mm for LM..A / NM..A / SM..A / GM..A / EF..A / GK..A anti-rotation brackets 228x20 mm, bolts short incl. 2 screws Multipack 20 pcs.
Z-ARS230L | Anti-rotation mechanism 230 mm for NF..A / SF..A anti-rotation brackets 228x20 mm, bolts long incl. 2 screws Multipack 20 pcs.
Z-AS1 | End stop kit for SH.. Comprised of: End stop SH Pan head screw M3x5 (Torx T10) only for open/close and -MP types Multipack 20 pcs.
Z-AS2 | End stop kit for LH..A / CH.. Comprised of: End stop LH / CH Pan head screw M3x5 (Torx T10) only for open/close and -MP types Multipack 20 pcs.
Z-DS1 | Rotary support for linear actuator for compensation of transverse forces with thread M6 incl. 1 bolt and 2 screws M6x10 mm
Z-EM-C1050 | Cabinet for Belimo Energy Manifold for max. 12 zones Galvanised sheet steel
Z-EM-C1200 | Cabinet for Belimo Energy Manifold for max. 12 zones Galvanised sheet steel
Z-EM-C600 | Cabinet for Belimo Energy Manifold for max. 5 zones Galvanised sheet steel
Z-EM-C750 | Cabinet for Belimo Energy Manifold for max. 7 zones Galvanised sheet steel
Z-EM-C900 | Cabinet for Belimo Energy Manifold for max. 11 zones Galvanised sheet steel
Z-ESCM | End stop clip for CM.. / CH.. / CQ.. / CQK.. / KR.. / UM.. Thermo-plastic material Multipack 20 pcs.
Z-ESUH | End stop clip for UH.. Thermo-plastic material Multipack 20 pcs.
Z-FKCH | Spring clip for CH.. Tempered steel Multipack 20 pcs.
Z-GMA | Baseplate extension from GM..A to GM.. incl. 2 screws Galvanised steel
Z-INSH15 | Insulation shell for EPIV / Belimo Energy Valve™ 2-way DN 15...25 only for non-condensing applications
Z-INSH32 | Insulation shell for EPIV / Belimo Energy Valve™ 2-way DN 32...50 only for non-condensing applications
Z-KB-PG11 | Cable gland incl. gland for cable diameter ø4...10 mm suitable for screw connections PG11
Z-KS1 | Coupling piece M8 for SH.. Fork head, axial joint with internal thread M8 twin fixing bolts retaining clip
Z-KS2 | Coupling piece M6 for LH..A / CH.. Fork head, axial joint with internal thread M6 twin fixing bolts retaining clip
Z-MA | Gear train disengagement magnet for CM.. / CH.. / CM..D.. Thermo-plastic material Nickel-plated magnet Multipack 20 pcs.
Z-NMA | Baseplate extension from NM..A to NM.. from LMQ..A to NMQB.. incl. 1 screw Galvanised steel
Z-PCUM | Protective covering for UM.. / UH.. Thermo-plastic material Multipack 20 pcs.
Z-PI | Position indicator for LM..A, NM..A, SM..A, GM..A Multipack 20 pcs.
Z-PICM | Position indicator for CM.. / UM.. with gear train disengagement magnet Thermo-plastic material Nickel-plated magnet Multipack 20 pcs.
Z-SF | Baseplate extension from NF..A / SF..A to NF.. / AF.. incl. 1 screw and 1 nut Galvanised steel
Z-SMA | Baseplate extension from SM..A to SM.. / AM.. incl. 2 screws Galvanised steel
Z-SPA | Adapter for auxiliary switch and feedback potentiometer if shaft clamp mounted below on xMQ..A.., NKQ..A.., GK..A.. Thermo-plastic material Multipack 20 pcs.
Z-STRJ.1 | Grommet for RJ connection module Multipack 50 pcs.
Z-TP | Terminal protection IP54 for actuators with terminals for cable diameters ø4...6 mm, ø6...8 mm, ø8...10 mm Multipack 20 pcs.
Z-UIC | Signal converter voltage/current 4...20 mA, Supply AC/DC 24 V Input 0(2)...10 V or 0(4)...20 mA Output 0(4)...20 mA no galvanic isolation Terminals 1.5 mm²
ZA-LM | Shaft adapter for LM..A Shaft adapter length = 50 mm for short damper shafts 8x8 mm, < 35 mm length for LM...-shaft clamp versions ø16 mm
ZA10-B | Form fit insert for BFL for hollow shaft 12x12 mm Reduction to 10x10 mm
ZA10-B.1 | Form fit insert for BFL for hollow shaft 12x12 mm Reduction to 10x10 mm Multipack 50 pcs.
ZA11-B | Form fit insert for BFL, BFN for hollow shaft 12x12 mm Reduction to 11x11 mm
ZA11-B.1 | Form fit insert for BFL, BFN for hollow shaft 12x12 mm Reduction to 11x11 mm Multipack 50 pcs.
ZA12ON-B.1 | Form fit insert without cams for BFL for hollow shaft 12x12 mm Reduction to 10x10 mm Multipack 100 pcs.
ZA18-BF | Adapter for BFL, BLF, BFN, BF, BLE, BEN, BEE for form fit 12 mm on round shaft 18 mm, L = 33 mm
ZA8-B | Form fit insert for BFL for hollow shaft 12x12 mm Reduction to 8x8 mm
ZA8-B.1 | Form fit insert for BFL for hollow shaft 12x12 mm Reduction to 8x8 mm Multipack 50 pcs.
ZBAE0 | Blanking cover for BAE (without thermal fuse for duct inside temperature)
ZBAE72 | Spare tripping element for BAE Duct inside temperature 72°C (colour black) Probe length 65 mm
ZBAE72/9 | Spare tripping element for BAE Duct inside temperature 72°C (colour black) Probe length 90 mm
ZBAE95 | Spare tripping element for BAE Duct inside temperature 95°C (colour green) Probe length 65 mm
ZBAE95/9 | Spare tripping element for BAE Duct inside temperature 95°C (colour green) Probe length 90 mm
ZBAT0 | Blanking cover for BAT (without thermal fuse for duct inside temperature)
ZBAT120 | Spare tripping element for BAT Duct inside temperature 120°C (colour orange) Probe length 65 mm
ZBAT120.1 | Spare tripping element for BAT Duct inside temperature 120°C (colour orange) Probe length 65 mm Multipack 20 pcs.
ZBAT140 | Spare tripping element for BAT Duct inside temperature 140°C (colour red) Probe length 65 mm
ZBAT72 | Spare tripping element for BAT Duct inside temperature 72°C (colour black) Probe length 65 mm
ZBAT72.1 | Spare tripping element for BAT Duct inside temperature 72°C (colour black) Probe length 65 mm Multipack 20 pcs.
ZBAT72/9 | Spare tripping element for BAT Duct inside temperature 72°C (colour black) Probe length 90 mm
ZBAT95 | Spare tripping element for BAT Duct inside temperature 95°C (colour grey) Probe length 65 mm
ZBAT95.1 | Spare tripping element for BAT Duct inside temperature 95°C (colour grey) Probe length 65 mm Multipack 20 pcs.
ZBAT95/9 | Spare tripping element for BAT Duct inside temperature 95°C (colour grey) Probe length 90 mm
ZCQ-C | End stop clip for CQ.. actuator Thermo-plastic material Multipack 5 pcs.
ZCQ-E | Spindle extension CQ Fluid temperature -20...90°C Thermo-plastic material
ZCQ-FL | Flow limiter PIQCV Manual flow rate setting
ZCQ-W | Housing cover CQ Colour: white (RAL 9010) Thermo-plastic material
ZD6N-H100 | Lever for butterfly valves DN 25...100 Manufacturer Belimo Type ZD6N-H100
ZD6N-H150 | Lever for butterfly valves DN 125...150 Manufacturer Belimo Type ZD6N-H150
ZD6N-S100 | Worm gear for butterfly valves DN 25...100 Self-locking, maintenance-free Gear ratio 24:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S100
ZD6N-S150 | Worm gear for butterfly valves DN 125...300 Self-locking, maintenance-free Gear ratio 24:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S150
ZD6N-S350 | Worm gear for butterfly valves DN 350 Self-locking, maintenance-free Gear ratio 50:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S350
ZD6N-S400 | Worm gear for butterfly valves DN 400 Self-locking, maintenance-free Gear ratio 80:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S400
ZD6N-S450 | Worm gear for butterfly valves DN 450 Self-locking, maintenance-free Gear ratio 80:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S450
ZD6N-S500 | Worm gear for butterfly valves DN 500 Self-locking, maintenance-free Gear ratio 560:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S500
ZD6N-S600 | Worm gear for butterfly valves DN 600 Self-locking, maintenance-free Gear ratio 640:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S600
ZD6N-S700 | Worm gear for butterfly valves DN 700 Self-locking, maintenance-free Gear ratio 704:1 Epoxy powder coating (black RAL 9005) not suitable for outdoor applications Manufacturer Belimo Type ZD6N-S700
ZD7100 | T-piece DN 100 Flange PN 16 for 3-way butterfly valve
ZD7125 | T-piece DN 125 Flange PN 16 for 3-way butterfly valve
ZD7150 | T-piece DN 150 Flange PN 16 for 3-way butterfly valve
ZD7200 | T-piece DN 200 Flange PN 16 for 3-way butterfly valve
ZD7250 | T-piece DN 250 Flange PN 16 for 3-way butterfly valve
ZD7300 | T-piece DN 300 Flange PN 16 for 3-way butterfly valve
ZDB-AF | Angle of rotation limiter for AF.. Galvanised steel
ZDB-LF | Angle of rotation limiter for LF.., with end stop Galvanised steel
ZDB-TF | Angle of rotation limiter for TF.., with end stop Galvanised steel
ZDF-09 | Form fit adapter flat head for DR..-R 9xø12x30 mm (WxøxH)
ZDF-11 | Form fit adapter flat head for DR..-R 11xø15x22 mm (WxøxH)
ZDV-01 | Form fit adapter flat head for DR..-R 13xø19x33 mm (WxøxH)
ZDV-02 | Form fit adapter square for DR..-R 17x17x19 mm (LxWxH)
ZDV-03 | Form fit adapter flat head for DR..-R 17xø22x33 mm (WxøxH)
ZDV-04 | Form fit adapter flat head for DR..-R 14xø18x33 mm (WxøxH)
ZF10-LMA | Form fit insert for LM..A, TM..A Thermo-plastic material Multipack 20 pcs.
ZF10-NSA | Form fit insert for LMQ..A / NM..A / SM..A Thermo-plastic material Multipack 20 pcs.
ZF10-NSA-F | Form fit insert for NF..A / SF..A Thermo-plastic material Multipack 20 pcs.
ZF12-LMA | Form fit insert for LM..A, TM..A Thermo-plastic material Multipack 20 pcs.
ZF12-NSA | Form fit insert for LMQ..A / NM..A / SM..A Thermo-plastic material Multipack 20 pcs.
ZF12-NSA-F | Form fit insert for NF..A / SF..A Thermo-plastic material Multipack 20 pcs.
ZF15-NSA | Form fit insert for LMQ..A / NM..A / SM..A Thermo-plastic material Multipack 20 pcs.
ZF15-NSA-F | Form fit insert for NF..A / SF..A Thermo-plastic material Multipack 20 pcs.
ZF16-NSA | Form fit insert for LMQ..A / NM..A / SM..A Thermo-plastic material Multipack 20 pcs.
ZF16-NSA-F | Form fit insert for NF..A / SF..A Thermo-plastic material Multipack 20 pcs.
ZF8-LF | Form fit adapter for damper shafts, with form fit 8x8 mm for LF.. Galvanised steel
ZF8-LMA | Form fit insert for LM..A, TM..A Thermo-plastic material Multipack 20 pcs.
ZF8-NMA | Form fit insert for LMQ..A / NM..A Thermo-plastic material Multipack 20 pcs.
ZF8-TF | Form fit adapter with form-fit 8x8 mm for TF.. Galvanised steel
ZFP2-MP | Connecting board MP-Bus for wiring boxes EXT-WR-FP..-MP Connection of 2 MP actuators incl. sensors Service socket for Belimo tools Connection of MP actuators via connector
ZFRL10-LMA | Form fit insert for LM..A, TM..A with angle of rotation limiter and position indicator Thermo-plastic material Multipack 20 pcs.
ZFRL12-LMA | Form fit insert for LM..A, TM..A with angle of rotation limiter and position indicator Thermo-plastic material Multipack 20 pcs.
ZFRL8-LMA | Form fit insert for LM..A, TM..A with angle of rotation limiter and position indicator Thermo-plastic material Multipack 20 pcs.
ZG-AF | Mounting kit for linkage operation for AF..
ZG-AFB | Mounting kit for linkage operation for flat and side installation
ZG-EFB | Mounting kit for linkage operation for flat and side installation
ZG-GMA | Mounting kit for linkage operation for flat installation
ZG-LF1 | Mounting kit for linkage operation for flat installation
ZG-LF3 | Mounting kit for linkage operation for side installation
ZG-NMA | Mounting kit for linkage operation for flat installation
ZG-SMA | Mounting kit for linkage operation for flat installation
ZG-TF1 | Mounting kit for linkage operation for flat and side installation
ZG-VRU01 | Dummy plug for VST connector plug for applications without actuator Multipack 25 pcs.
ZGF-08 | Form fit adapter flat head for GR..-R 8xø11x33 mm (WxøxH)
ZGF-14 | Form fit adapter flat head for GR..-R 14xø18x33 mm (WxøxH)
ZGF-17 | Form fit adapter flat head for GR..-R 17xø22x33 mm (WxøxH)
ZGI-001 | Reducer for form fit adapter ZGV-19 14x14x20 mm (LxWxH)
ZGI-002 | Reducer for form fit adapter ZGV-16 11x11x20 mm (LxWxH)
ZGI-003 | Reducer for form fit adapter ZGV-19 14x14x35 mm (LxWxH)
ZGI-004 | Reducer for form fit adapter ZGV-16 11x11x35 mm (LxWxH)
ZGI-009 | Reducer for form fit adapter ZGV-19 11xø17x15 mm (WxøxH)
ZGI-010 | Reducer for form fit adapter ZGV-19 10xø17x15 mm (WxøxH)
ZGI-012 | Reducer for form fit adapter ZGV-19 12x12x35 mm (LxWxH)
ZGI-013 | Reducer for form fit adapter ZGV-16 10x10x15 mm (LxWxH)
ZGI-014 | Reducer for form fit adapter ZGV-19 8xø17x15 mm (WxøxH)
ZGI-015 | Reducer for form fit adapter ZGV-19 9xø17x15 mm (WxøxH)
ZGV-14 | Form fit adapter square for GR..-R 14x14x40 mm (LxWxH)
ZGV-16 | Form fit adapter square for GR..-R 16x16x40 mm (LxWxH)
ZGV-17 | Form fit adapter square for GR..-R 17x17x20 mm (LxWxH)
ZGV-19 | Form fit adapter square for GR..-R 19x19x40 mm (LxWxH)
ZH24-1 | Stem heater DN 15...50 AC/DC 24 V, 45 W
ZH24-1-A | Stem heater AC/DC 24 V, 30 W
ZH24-1-B | Stem heater AC/DC 24 V, 60 W
ZH24-1-C | Stem heater DN 65...100 AC 24 V, 60 W
ZH24-1-D | Stem heater DN 125...250 AC 24 V, 60 W
ZH4515 | Pipe connector DN 15 for globe valve with external thread Malleable cast iron, galvanized
ZH4520 | Pipe connector DN 20 for globe valve with external thread Malleable cast iron, galvanized
ZH4525 | Pipe connector DN 25 for globe valve with external thread Malleable cast iron, galvanized
ZH4532 | Pipe connector DN 32 for globe valve with external thread Malleable cast iron, galvanized
ZH4540 | Pipe connector DN 40 for globe valve with external thread Malleable cast iron, galvanized
ZH4550 | Pipe connector DN 50 for globe valve with external thread Malleable cast iron, galvanized
ZH515 | Blanking connection DN 15 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH520 | Blanking connection DN 20 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH525 | Blanking connection DN 25 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH532 | Blanking connection DN 32 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH540 | Blanking connection DN 40 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH550 | Blanking connection DN 50 for globe valve with external thread for conversion to 2-way valve Malleable cast iron, galvanized
ZH7100 | Blanking flange PN 16 DN 100 for globe valve for conversion to 2-way valve
ZH7125 | Blanking flange PN 16 DN 125 for globe valve for conversion to 2-way valve
ZH715 | Blanking flange PN 16 DN 15 for globe valve for conversion to 2-way valve
ZH7150 | Blanking flange PN 16 DN 150 for globe valve for conversion to 2-way valve
ZH720 | Blanking flange PN 16 DN 20 for globe valve for conversion to 2-way valve
ZH725 | Blanking flange PN 16 DN 25 for globe valve for conversion to 2-way valve
ZH732 | Blanking flange PN 16 DN 32 for globe valve for conversion to 2-way valve
ZH740 | Blanking flange PN 16 DN 40 for globe valve for conversion to 2-way valve
ZH750 | Blanking flange PN 16 DN 50 for globe valve for conversion to 2-way valve
ZH765 | Blanking flange PN 16 DN 65 for globe valve for conversion to 2-way valve
ZH780 | Blanking flange PN 16 DN 80 for globe valve for conversion to 2-way valve
ZIP-BT-NFC
ZJR01
ZJR03
ZJR20
ZK-BF | Adapter for BF, BLF for form fit with clamp for round shaft 10...20 mm / square 10...16 mm
ZK1-B | Hand crank 40 mm for BLF, BF, BLE, BE
ZK1-B.1 | Hand crank 40 mm for BLF, BF, BLE, BE Multipack 100 pcs.
ZK1-GEN | Connecting cable 5 m A: RJ11 6/4 ZTH EU B: 6-pin for connection to service socket
ZK1-VAV | Connecting cable 5 m A: RJ11 6/4 ZTH EU B: 3-pin service plug NMV-D2M, CR..
ZK2-B | Hand crank 70 mm for BLF, BF, BLE, BE
ZK2-B.1 | Hand crank 70 mm for BLF, BF, BLE, BE Multipack 100 pcs.
ZK2-GEN | Connecting cable 5 m A: RJ11 6/4 ZTH EU B: free wire end for connection to MP/PP terminal
ZK4-GEN | Connecting cable 3 m A: RJ11 6/4 ZTH EU B: 3-pin Weidmüller and supply connection
ZK6-GEN | Connecting cable 5 m A+B: RJ12 6/6
ZKN1-B | Hand crank 40 mm for BFL, BFN, BEN, BEE
ZKN1-B.1 | Hand crank 40 mm for BFL, BFN, BEN, BEE Multipack 100 pcs.
ZKN2-B | Hand crank 63 mm for BFL, BFN, BEN, BEE
ZKN2-B.1 | Hand crank 63 mm for BFL, BFN, BEN, BEE Multipack 100 pcs.
ZLR-01 | Connection adapter QCV-LR
ZN230-24 | Plug-in power supply unit for MFT-C Input voltage AC 230 V Output voltage AC 24 V / 14 VA
ZN230-24MP | MP-Bus power supply for MP actuators AC 24/230 V for local power supply of one MP actuator during operation on MP-Bus AC 230 V (connection: cable with Euro plug)
ZNV-203 | Spacer ring for LDM, stroke 20 mm
ZNV-204 | Spacer ring for Sauter, stroke 20 mm
ZNV-205 | Adapter kit Danfoss
ZNV-206 | Adapter kit IMI / Elesta
ZNV-207 | Stem Adapter for LV..-RE, NV..-RE, SV..-RE
ZNV-C | Spare coupling for LV.., NV.., SV.. actuator
ZPD-RE2 | Differential pressure pickup device for VAV-RetroFIT+ for round boxes up to 400 mm Multipack 18 pcs.
ZPD-RE2-SET | Differential pressure pickup device for VAV-RetroFIT+ for round boxes up to 400 mm
ZPF-08 | Form fit adapter flat head for SR..P..-R 8xø17x57 mm (WxøxH)
ZPF-09 | Form fit adapter flat head for SR..P..-R 9xø12x57 mm (WxøxH)
ZPF-10 | Form fit adapter flat head for SR..P..-R 10xø17x57 mm (WxøxH)
ZPF-11 | Form fit adapter flat head for SR..P..-R 11xø14x57 mm (WxøxH)
ZPF-14 | Form fit adapter flat head for SR..P..-R 14xø18x57 mm (WxøxH)
ZPK-12 | Form fit adapter wedge groove for SR..P..-R ø12x4x57 mm (øxWxH)
ZPK-14 | Form fit adapter wedge groove for SR..P..-R ø14x5x57 mm (øxWxH)
ZPR01 | Position indicator and tappet shaft F07, square 45° offset, SW 17 DN 125...300
ZPR02 | Tappet shaft F07, square 45° offset, SW 17
ZPR03 | Position indicator and tappet shaft F05, square 45° offset, SW 14 DN 80...100
ZPR05 | RetroFIT+ adapter kit for PR.. F07/F10 (incl. screws F07), flat head/square, SW 17
ZPR06 | RetroFIT+ adapter kit for PR.. F07/F10 (incl. screws F07), square 45° offset, SW 14
ZPR08 | Adapter kit with spacer ring for PR.. F07, square 45° offset, SW 17
ZPR09 | RetroFIT+ adapter kit for PR.. F07/F05/F10 (incl. screws F07), flat head/square, SW 14
ZPR10 | RetroFIT+ adapter kit for PR.. F05/F07/F10 (incl. screws F05), flat head/square, SW 14
ZPR11 | RetroFIT+ adapter kit for PR.. F07/F10 (incl. screws F07), square 45° offset, SW 18
ZPR12 | RetroFIT+ adapter kit for PR.. F07/F10 (incl. screws F07), flat head/square, SW 16
ZPR13 | RetroFIT+ adapter kit for PR.. F07/F05/F10 (incl. screws F07), flat head/square, SW 11
ZPR14 | RetroFIT+ adapter kit for PR.. F07/F05/F10 (incl. screws F07), flat head/square, SW 12.7
ZPR15 | RetroFIT+ adapter kit for PR.. F07/F10 (incl. screws F07), square 45° offset, SW 11
ZPR20 | Hand crank for PR/PM actuator
ZPV-08 | Form fit adapter square for SR..P..-R 8x8x57 mm (LxWxH)
ZPV-09 | Form fit adapter square for SR..P..-R 9x9x57 mm (LxWxH)
ZPV-10 | Form fit adapter square for SR..P..-R 10x10x57 mm (LxWxH)
ZPV-11 | Form fit adapter square for SR..P..-R 11x11x57 mm (LxWxH)
ZPV-12 | Form fit adapter square for SR..P..-R 12x12x57 mm (LxWxH)
ZPV-14 | Form fit adapter square for SR..P..-R 14x14x57 mm (LxWxH)
ZR-004 | Fixing bracket for 6-way valve Blue galvanised steel
ZR-005 | Fixing bracket for 6-way valve Stainless steel
ZR-EXT-01 | Valve neck extension for ball valve DN 15...50
ZR-EXT-F05 | Valve neck extension for ball valve DN 65...150 for butterfly valves up to DN 80
ZR2315 | Pipe connector DN 15 for ball valve with internal thread Nickel-plated brass
ZR2320 | Pipe connector DN 20 for ball valve with internal thread Nickel-plated brass
ZR2325 | Pipe connector DN 25 for ball valve with internal thread Nickel-plated brass
ZR2332 | Pipe connector DN 32 for ball valve with internal thread Nickel-plated brass
ZR2340 | Pipe connector DN 40 for ball valve with internal thread Nickel-plated brass
ZR2350 | Pipe connector DN 50 for ball valve with internal thread Nickel-plated brass
ZR24-2 | Stem heater incl. retaining clip DN 15...50 AC/DC 24 V, 20 W
ZR24-F05 | Stem heater flange ISO 5211, F05 AC/DC 24 V, 30 W
ZR4510 | Pipe connector DN 10 for ball valve with external thread Nickel-plated brass
ZR4515 | Pipe connector DN 15 for ball valve with external thread Nickel-plated brass
ZR4515Q | Pipe connector DN 15 for ball valve with external thread Nickel-plated brass
ZR4520 | Pipe connector DN 20 for ball valve with external thread Nickel-plated brass
ZR4520Q | Pipe connector DN 20 for ball valve with external thread Nickel-plated brass
ZR4525 | Pipe connector DN 25 for ball valve with external thread Nickel-plated brass
ZR4532 | Pipe connector DN 32 for ball valve with external thread Nickel-plated brass
ZR4540 | Pipe connector DN 40 for ball valve with external thread Nickel-plated brass
ZR4550 | Pipe connector DN 50 for ball valve with external thread Nickel-plated brass
ZR6065
ZR6080
ZR6100
ZR6125
ZR6150
ZREV15F | Pipe connector DN 15 Internal thread PN 25 Nickel-plated brass
ZREV20F | Pipe connector DN 20 Internal thread PN 25 Nickel-plated brass
ZREV25F | Pipe connector DN 25 Internal thread PN 25 Nickel-plated brass
ZREV32F | Pipe connector DN 32 Internal thread PN 25 Nickel-plated brass
ZREV40F | Pipe connector DN 40 Internal thread PN 25 Nickel-plated brass
ZREV50F | Pipe connector DN 50 Internal thread PN 25 Nickel-plated brass
ZRI-001 | Spacer ring Height 22 mm F04/F05
ZRI-002 | Spacer ring Height 23.5 mm F05/F07
ZRV-301 | Spacer ring for Sauter, stroke 50 mm
ZRV-302 | Spacer ring for Siebe, stroke 50 mm
ZRV-303 | Spacer ring for Johnson Control, stroke 50 mm
ZRV-304 | Washer Sauter for Sauter, stroke 50 mm
ZSD-B.1 | Protective bag with wire Dimensions LxW approx. 350x250 mm Multipack 100 pcs.
ZSF-08 | Form fit adapter flat head for SR..-R 8xø17x57 mm (WxøxH)
ZSF-09 | Form fit adapter flat head for SR..-R 9xø12x57 mm (WxøxH)
ZSF-10 | Form fit adapter flat head for SR..-R 10xø17x57 mm (WxøxH)
ZSF-11 | Form fit adapter flat head for SR..-R 11xø14x57 mm (WxøxH)
ZSF-14 | Form fit adapter flat head for SR..-R 14xø18x57 mm (WxøxH)
ZSFF-08 | Form fit adapter flat head for SRF..-R 8xø17x55 mm (WxøxH)
ZSFF-09 | Form fit adapter flat head for SRF..-R 9xø12x55 mm (WxøxH)
ZSFF-10 | Form fit adapter flat head for SRF..-R 10xø17x55 mm (WxøxH)
ZSFF-11 | Form fit adapter flat head for SRF..-R 11xø14x55 mm (WxøxH)
ZSFF-14 | Form fit adapter flat head for SRF..-R 14xø18x55 mm (WxøxH)
ZSFK-12 | Form fit adapter wedge groove for SRF..-R ø12x4x55 mm (øxWxH)
ZSFK-14 | Form fit adapter wedge groove for SRF..-R ø14x5x55 mm (øxWxH)
ZSFV-08 | Form fit adapter square for SRF..-R 8x8x55 mm (LxWxH)
ZSFV-09 | Form fit adapter square for SRF..-R 9x9x55 mm (LxWxH)
ZSFV-10 | Form fit adapter square for SRF..-R 10x10x55 mm (LxWxH)
ZSFV-11 | Form fit adapter square for SRF..-R 11x11x55 mm (LxWxH)
ZSFV-12 | Form fit adapter square for SRF..-R 12x12x55 mm (LxWxH)
ZSFV-14 | Form fit adapter square for SRF..-R 14x14x55 mm (LxWxH)
ZSG-GMA-DE | Protective housing for GM..A
ZSG-LMA-DE | Protective housing for LM..A
ZSG-NMA-DE | Protective housing for NM..A
ZSG-NSA-F-DE | Protective housing for NF..A / SF..A
ZSG-RM-DE | Protective housing for LR.., NR.., SR..
ZSG-SMA-DE | Protective housing for SM..A
ZSK-12 | Form fit adapter wedge groove for SR..-R ø12x4x57 mm (øxWxH)
ZSK-14 | Form fit adapter wedge groove for SR..-R ø14x5x57 mm (øxWxH)
ZSN-B | Bracket for SN2-C7 for BFN/BFL, BEN/BEE
ZSN-BF | Bracket for SN2-C7 for BF
ZST-BS | Cable set with plug 0.5 m for communication and power supply unit
ZSV-08 | Form fit adapter square for SR..-R 8x8x57 mm (LxWxH)
ZSV-09 | Form fit adapter square for SR..-R 9x9x57 mm (LxWxH)
ZSV-10 | Form fit adapter square for SR..-R 10x10x57 mm (LxWxH)
ZSV-11 | Form fit adapter square for SR..-R 11x11x57 mm (LxWxH)
ZSV-11-4K | Form fit adapter square for SR..-R 11x11x57 mm (LxWxH, inside square)
ZSV-12 | Form fit adapter square for SR..-R 12x12x57 mm (LxWxH)
ZSV-14 | Form fit adapter square for SR..-R 14x14x57 mm (LxWxH)
ZSY-001 | Adapter kit square 22x22 mm to square 14x14 mm
ZSY-005 | Mounting/adapter kit for SY2/3 square 22x22 mm to square 14x14 mm
ZSY-011 | Adapter kit with spacer ring for SY4/5/6 square 35x35 mm on flat head SW 22
ZSY-012 | Mounting/adapter kit for SY2/3 square 22x22 mm on flat head SW 17
ZSY-013 | Mounting/adapter kit for SY4/5/6 square 22x22 mm to square 17x17 mm
ZSY-014 | Insulation cover for ARI ZESA, GESA valves DN 125...200, PA 6GF50
ZSY-401 | Mounting/adapter kit for BFV D6400N/NL + SY6
ZSY-402 | Mounting/adapter kit for BFV D6450N/NL + SY5
ZSY-403 | Mounting/adapter kit for Victaulic Butterfly Valves
ZSY-404 | Mounting/adapter kit for Victaulic Butterfly Valves
ZSY-701 | Mounting/adapter kit for BFV D6400N/NL + SY7
ZSY-702 | Mounting/adapter kit for BFV D6450-500N/NL + SY7-8
ZSY-703 | Mounting/adapter kit for BFV D6350N/NL + SY7
ZSY-901 | Mounting/adapter kit for BFV D6500N/NL + SY9
ZSY-902 | Mounting/adapter kit for BFV D6600N/NL + SY10-12
ZSY-903 | Mounting/adapter kit for BFV D6700N/NL + SY12
ZTH EU | Service tool with ZIP-USB function for parametrisable and communicative Belimo actuators, VAV controller and HVAC performance devices Connection via service socket of the device or MP/PP-connection
ZWE50 | Sticker ta max. 50°C Roll of 1000 pcs.
ZZ12-B | Pointer for BLF, BF, BLE for hollow shaft 12x12 mm Material steel
ZZ12-B.1 | Pointer for BLF, BF, BLE for hollow shaft 12x12 mm Material steel Multipack 100 pcs.
ZZN12-B | Pointer for BFL, BFN, BEN, BEE for hollow shaft 12x12 mm Material polycarbonate
ZZN12-B.1 | Pointer for BFL, BFN, BEN, BEE for hollow shaft 12x12 mm Material polycarbonate Multipack 100 pcs.